## AGENT-GENERATE
Node | Design Intention | Parameter | Guide Word | Deviation | Cause | Consequence | Initial Severity | Initial Likelihood | Initial Risk Ranking | IPLs | IPL Independent | IPL Effective | IPL Auditable | Safeguards | Final Severity | Final Likelihood | Final Risk Ranking | Recommendations | Comments_Actions
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.1 F-N2 fouling or PV-N2-REG failing toward closed restricts nitrogen flow to the gas mixer and emergency purge header | 1.1.1 Reduced nitrogen dilution increases H2 fraction in TK-500L; flammable mixed gas may be routed to the downstream Process with fire or explosion potential | 5 | 1 | R1 | 1.1.1.1 H2A-1 high H2 analyzer with EC-1 automatic outlet isolation and alarmed response (-1) | Yes | Yes | Yes | 1.1.1.S1 PI-N2-1 local pressure indication; 1.1.1.S2 CD-1 and HMI-1 concentration display | 5 | 2 | R1 | 1.1.1.R1 Add independent low N2 pressure or low N2 flow trip to stop H2 feed and mixer before high H2 gas enters TK-500L | 1.1.1.A1 Verify analyzer voting response time and proof test basis for credited emergency isolation
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.1 F-N2 fouling or PV-N2-REG failing toward closed restricts nitrogen flow to the gas mixer and emergency purge header | 1.1.2 Total mixed gas rate falls and TK-500L pressure decays during downstream demand; the downstream Process may lose feed and trip production | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.2.S1 PI-N2-1 local pressure indication; 1.1.2.S2 operator observation of receiver outlet pressure trend | 2 | 1 | R2 | 1.1.2.R1 Define operating response for low N2 pressure and low receiver outlet pressure alarms if not already implemented | 1.1.2.A1 Production consequence depends on downstream Process tolerance for short mixed gas interruption
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.1 F-N2 fouling or PV-N2-REG failing toward closed restricts nitrogen flow to the gas mixer and emergency purge header | 1.1.3 Hydrogen enriched gas can remain in TK-500L and discharge through the roof vent during recovery; a flammable cloud or flash fire hazard may occur near the discharge point | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.1.3.S1 SV-21.2 and CV-12.2 vent path; 1.1.3.S2 FA-1 vent line device not credited until duty is confirmed | 4 | 1 | R1 | 1.1.3.R1 Confirm roof vent dispersion basis and confirm whether FA-1 is a certified flame arrester suitable for hydrogen service | 1.1.3.A1 FA-1 function is not legible enough to assign IPL credit
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.1 F-N2 fouling or PV-N2-REG failing toward closed restricts nitrogen flow to the gas mixer and emergency purge header | 1.1.4 Emergency flushing becomes ineffective and TK-500L may remain above the intended H2 concentration target; extended isolation and investigation create asset downtime | 3 | 1 | R2 | 1.1.4.1 H2A-1 high H2 alarm with trained operator action to stop H2 supply and mixer (-1) | Yes | Yes | Yes | 1.1.4.S1 EC-1 programmed 10 minute recovery sequence; 1.1.4.S2 HMI-1 abnormal condition indication | 3 | 2 | R2 | 1.1.4.R1 Provide a written abnormal operating procedure for failed H2 reduction after emergency purge demand | 1.1.4.A1 Do not credit the N2 purge itself because the initiating cause impairs the same nitrogen service
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.1 F-N2 fouling or PV-N2-REG failing toward closed restricts nitrogen flow to the gas mixer and emergency purge header | 1.1.5 Low N2 pressure can allow hydrogen migration toward the N2 feed branch when check valves are challenged; flammable gas may enter the customer nitrogen header | 4 | 1 | R1 | 1.1.5.1 CV-N2-IN backflow prevention on N2 feed (-1); 1.1.5.2 CV-12.3 backflow prevention on emergency N2 branch (-1) | Yes | Yes | Yes | 1.1.5.S1 PI-N2-1 local pressure indication; 1.1.5.S2 nitrogen SDS requirement for backflow prevention | 4 | 3 | R2 | 1.1.5.R1 Verify check valve specification inspection interval and tightness test requirement for hydrogen backflow prevention | 1.1.5.A1 Credit assumes check valves are independent from the N2 regulator or filter restriction
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.2 F-H2 fouling or PV-H2-REG or SV-H2-IN failing closed restricts hydrogen flow to MG-100-2ME(Ex) | 1.2.1 TK-500L receives nitrogen rich gas and the downstream Process receives off specification low H2 gas; production quality and conversion may be lost | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.1.S1 H2A-1 concentration indication; 1.2.1.S2 CD-1 and HMI-1 operator display | 2 | 1 | R2 | 1.2.1.R1 Establish low H2 concentration alarm set point and operator response for off specification mixed gas | 1.2.1.A1 H2 analyzer is treated as monitoring only unless low H2 alarm action is defined and tested
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.2 F-H2 fouling or PV-H2-REG or SV-H2-IN failing closed restricts hydrogen flow to MG-100-2ME(Ex) | 1.2.2 Flow imbalance and restart of the H2 line can create a transient high H2 slug to TK-500L; flammable gas may reach the downstream Process | 4 | 1 | R1 | 1.2.2.1 H2A-1 high H2 analyzer with EC-1 automatic closure of SV-21.1 and alarmed response (-1) | Yes | Yes | Yes | 1.2.2.S1 H2A-1 auto calibration feature; 1.2.2.S2 PI-H2-1 local pressure indication | 4 | 2 | R2 | 1.2.2.R1 Confirm restart permissive prevents opening H2 feed until stable N2 flow and analyzer validation are achieved | 1.2.2.A1 IPL credit applies only to high H2 transient after flow recovery
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.2 F-H2 fouling or PV-H2-REG or SV-H2-IN failing closed restricts hydrogen flow to MG-100-2ME(Ex) | 1.2.3 Downstream equipment dependent on hydrogen can be starved of required component; process upset or equipment damage may occur | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.3.S1 downstream Process interface pressure indication if available; 1.2.3.S2 HMI-1 concentration trend | 3 | 1 | R2 | 1.2.3.R1 Confirm downstream Process trip philosophy for loss of required H2 concentration | 1.2.3.A1 Consequence severity should be confirmed with downstream unit owner
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.2 F-H2 fouling or PV-H2-REG or SV-H2-IN failing closed restricts hydrogen flow to MG-100-2ME(Ex) | 1.2.4 H2 regulator and solenoid cycling during restricted feed can impose pressure transients on hydrogen piping; small fitting leakage may form an invisible jet fire if ignited | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.2.4.S1 PI-H2-1 local pressure indication; 1.2.4.S2 Ex rated MG-100-2ME(Ex) equipment selection | 4 | 1 | R1 | 1.2.4.R1 Consider hydrogen leak detection and define inspection frequency for H2 regulator and solenoid valve connections | 1.2.4.A1 No fixed hydrogen detector or automatic isolation on leak is listed in the provided node data
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.2 F-H2 fouling or PV-H2-REG or SV-H2-IN failing closed restricts hydrogen flow to MG-100-2ME(Ex) | 1.2.5 Receiver pressure can fall below downstream Process pressure during demand; reverse contamination toward TK-500L may occur if outlet backflow is not prevented | 4 | 1 | R1 | 1.2.5.1 CV-12.1 normal outlet check valve for process backflow prevention (-1) | Yes | Yes | Yes | 1.2.5.S1 PI-OUT-1 local pressure indication; 1.2.5.S2 operator monitoring of receiver outlet pressure | 4 | 2 | R2 | 1.2.5.R1 Verify CV-12.1 cracking pressure orientation and inspection basis against reverse flow from the downstream Process | 1.2.5.A1 Credit assumes CV-12.1 is not the failed element in this initiating cause
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.3 SV-27 fails closed or remains shut on the mixed gas transfer line from MG-100-2ME(Ex) to TK-500L | 1.3.1 TK-500L receives no replenishment and receiver pressure falls during downstream demand; mixed gas supply to the downstream Process is interrupted | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.1.S1 PI-OUT-1 local receiver outlet pressure indication; 1.3.1.S2 HMI-1 valve status if configured | 2 | 1 | R2 | 1.3.1.R1 Add clear alarm indication for SV-27 closed status during normal production mode | 1.3.1.A1 Consequence is primarily operability and production continuity
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.3 SV-27 fails closed or remains shut on the mixed gas transfer line from MG-100-2ME(Ex) to TK-500L | 1.3.2 The mixer outlet is blocked while gas feeds continue; pressure can rise in the mixer discharge line and a flammable H2 containing release may occur | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.3.2.S1 1 inch S316L schedule 10 piping specification; 1.3.2.S2 PI-H2-1 and PI-N2-1 local pressure indications | 4 | 1 | R1 | 1.3.2.R1 Verify pressure relief or automatic feed shutdown basis for blocked SV-27 with both gas supplies available | 1.3.2.A1 No dedicated relief device on the mixer discharge line is identified in the supplied data
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.3 SV-27 fails closed or remains shut on the mixed gas transfer line from MG-100-2ME(Ex) to TK-500L | 1.3.3 Mixer backpressure can disturb feed regulator balance and challenge branch check valves; hydrogen may migrate into the nitrogen side or nitrogen may enter the hydrogen branch | 4 | 1 | R1 | 1.3.3.1 CV-N2-IN check valve on nitrogen feed (-1); 1.3.3.2 CV-H2-IN check valve on hydrogen feed (-1) | Yes | Yes | Yes | 1.3.3.S1 PI-N2-1 and PI-H2-1 local pressure indications | 4 | 3 | R2 | 1.3.3.R1 Confirm check valve material compatibility and periodic functional testing for bidirectional cross contamination prevention | 1.3.3.A1 Credit assumes check valves are maintained and independent of SV-27 failure
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.3 SV-27 fails closed or remains shut on the mixed gas transfer line from MG-100-2ME(Ex) to TK-500L | 1.3.4 Stagnant gas remains in TK-500L and may be sent to the downstream Process after SV-27 is reopened; off specification or flammable composition excursion may occur | 3 | 1 | R2 | 1.3.4.1 H2A-1 concentration analyzer alarm with operator verification before restoring outlet flow (-1) | Yes | Yes | Yes | 1.3.4.S1 CD-1 and HMI-1 display of receiver H2 concentration; 1.3.4.S2 auto calibration feature | 3 | 2 | R2 | 1.3.4.R1 Add restart checklist requiring analyzer confirmation before opening SV-21.1 after SV-27 blockage | 1.3.4.A1 Analyzer credit requires the alarm to be independent of the SV-27 initiating failure
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.3 SV-27 fails closed or remains shut on the mixed gas transfer line from MG-100-2ME(Ex) to TK-500L | 1.3.5 Prolonged loss of receiver inflow can force downstream Process shutdown and manual troubleshooting near hydrogen containing equipment | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.5.S1 HMI-1 abnormal valve status if provided; 1.3.5.S2 local pressure indicators | 3 | 1 | R2 | 1.3.5.R1 Define safe troubleshooting isolation and gas testing steps before local intervention around MG-100-2ME(Ex) and TK-500L | 1.3.5.A1 Human exposure during troubleshooting should be controlled by procedure and portable gas testing
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.4 SV-21.1 fails closed or CV-12.1 remains shut on the normal receiver outlet to the downstream Process | 1.4.1 Normal mixed gas delivery stops and the downstream Process loses its 4.5-5 bar supply; production interruption or unit trip may follow | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.1.S1 PI-OUT-1 local pressure indication; 1.4.1.S2 HMI-1 outlet valve status if configured | 2 | 1 | R2 | 1.4.1.R1 Provide clear low outlet flow or low downstream supply pressure alarm with operator action | 1.4.1.A1 No independent flow measurement on the normal outlet is listed
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.4 SV-21.1 fails closed or CV-12.1 remains shut on the normal receiver outlet to the downstream Process | 1.4.2 Continued mixer inflow into an isolated TK-500L can raise receiver pressure toward its 10 bar maximum; loss of containment of flammable gas may occur if pressure exceeds design limits | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.4.2.S1 TK-500L stainless steel receiver rated to 10 bar; 1.4.2.S2 PI-OUT-1 local pressure indication | 4 | 1 | R1 | 1.4.2.R1 Verify overpressure protection or automatic mixer shutdown for blocked normal outlet with continuing gas feed | 1.4.2.A1 No PSV or independent high pressure trip is identified for TK-500L in the supplied data
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.4 SV-21.1 fails closed or CV-12.1 remains shut on the normal receiver outlet to the downstream Process | 1.4.3 Hydrogen rich inventory can be retained in TK-500L and later vented or released during restart; flammable exposure may occur at the roof vent or process interface | 4 | 1 | R1 | 1.4.3.1 H2A-1 high H2 analyzer with EC-1 purge and roof vent sequence through SV-21.2 and SV-21.3 (-1) | Yes | Yes | Yes | 1.4.3.S1 CV-12.2 vent line check valve; 1.4.3.S2 FA-1 vent line device not credited until function is confirmed | 4 | 2 | R2 | 1.4.3.R1 Validate emergency purge and vent sequence for the case where SV-21.1 is already closed or failed shut | 1.4.3.A1 Credit assumes analyzer and emergency valves remain independent of the outlet valve failure
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.4 SV-21.1 fails closed or CV-12.1 remains shut on the normal receiver outlet to the downstream Process | 1.4.4 Downstream Process equipment can experience low pressure or gas starvation; process instability may create asset damage or controlled shutdown | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.4.S1 downstream Process check and trip functions if present outside this node; 1.4.4.S2 PI-OUT-1 local pressure indication | 3 | 1 | R2 | 1.4.4.R1 Confirm interface alarm responsibility between this package and downstream Process for loss of mixed gas supply | 1.4.4.A1 Downstream safeguards are not credited because they are outside the selected node boundary
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.4 SV-21.1 fails closed or CV-12.1 remains shut on the normal receiver outlet to the downstream Process | 1.4.5 Reduced outlet demand causes mixer and regulator cycling; vibration or pressure fluctuation may promote leakage at hydrogen service connections | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.5.S1 Ex rated MG-100-2ME(Ex) equipment; 1.4.5.S2 local pressure indicators on feed and outlet headers | 3 | 1 | R2 | 1.4.5.R1 Review regulator stability and solenoid valve cycling limits for blocked outlet operation | 1.4.5.A1 Leakage consequence is treated as an escalation from pressure cycling rather than generic deterioration
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.5 PS-1 electrical or control power loss de energizes MG-100-2ME(Ex) controls and solenoid valves causing package flow interruption | 1.5.1 Gas mixer operation and solenoid valve actuation cease; TK-500L and downstream Process lose normal mixed gas supply | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.1.S1 receiver inventory provides short buffer only; 1.5.1.S2 local pressure indicators remain useful only if visible and powered as applicable | 2 | 1 | R2 | 1.5.1.R1 Confirm fail safe positions of SV-N2-IN SV-H2-IN SV-27 SV-21.1 SV-21.2 and SV-21.3 on power loss | 1.5.1.A1 No UPS or redundant power supply is identified in the supplied package data
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.5 PS-1 electrical or control power loss de energizes MG-100-2ME(Ex) controls and solenoid valves causing package flow interruption | 1.5.2 H2A-1 CD-1 HMI-1 and EC-1 functions may be unavailable; abnormal H2 concentration can remain undetected and flammable gas may be present in TK-500L | 5 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.2.S1 auto calibration feature is not effective during loss of power; 1.5.2.S2 operator rounds if safely performed | 5 | 1 | R1 | 1.5.2.R1 Provide UPS backed analyzer and emergency logic or demonstrate valves fail to a safe purged and isolated condition on power loss | 1.5.2.A1 Analyzer based IPLs are not credited because the initiating cause disables the same control power source
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.5 PS-1 electrical or control power loss de energizes MG-100-2ME(Ex) controls and solenoid valves causing package flow interruption | 1.5.3 Emergency N2 purge and roof vent valve actuation may not occur during a high H2 condition; receiver gas cannot be diluted or safely displaced as intended | 5 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.3.S1 manual intervention may be possible only under controlled permit and gas testing; 1.5.3.S2 CV-12.3 and CV-12.2 provide passive backflow resistance only | 5 | 1 | R1 | 1.5.3.R1 Ensure emergency valves move to the required safe state on loss of power or provide independent pneumatic stored energy for purge and vent demand | 1.5.3.A1 No credit is assigned to EC-1 because the same power loss can disable the emergency sequence
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.5 PS-1 electrical or control power loss de energizes MG-100-2ME(Ex) controls and solenoid valves causing package flow interruption | 1.5.4 Fail closed valve positions can isolate compressed H2/N2 in TK-500L and short piping; pressure changes during standstill may result in flammable gas release at weak points | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.4.S1 TK-500L 10 bar mechanical rating; 1.5.4.S2 PI-OUT-1 local pressure indication if available after power loss | 4 | 1 | R1 | 1.5.4.R1 Define depressurization and isolation philosophy for loss of electrical power with compressed hydrogen containing inventory | 1.5.4.A1 Mechanical design margin is not credited as an IPL without documented design case verification
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) and TK-500L to downstream Process and roof vent | Provide filtered and regulated H2/N2 mixed gas to TK-500L and deliver 4.5-5 bar gas to downstream Process while enabling analyzer initiated outlet isolation N2 purge and roof venting | Flow | No/Low | 1. No/Low Flow | 1.5 PS-1 electrical or control power loss de energizes MG-100-2ME(Ex) controls and solenoid valves causing package flow interruption | 1.5.5 Loss of display and control indication delays diagnosis and can require local manual troubleshooting near hydrogen and nitrogen services; personnel may be exposed to flammable gas or oxygen displacement hazard | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.5.S1 portable gas testing and permit controls if required by site practice; 1.5.5.S2 local pressure indicators for field confirmation | 3 | 1 | R2 | 1.5.5.R1 Add emergency response procedure requiring area gas testing ventilation and isolation before local troubleshooting after power failure | 1.5.5.A1 Nitrogen is an asphyxiant and hydrogen is extremely flammable so manual response should be minimized and proceduralized
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.1 PV-H2-REG fails open or is set too high on the hydrogen feed to MG-100-2ME(Ex) | 1.1.1 Receiver H2 concentration increases above the intended mixture; downstream Process may receive gas within the flammable range; ignition can cause fire or explosion | 4 | 1 | R1 | 1.1.1.1 H2A-1 high H2 detection with EC-1 action to close SV-21.1 and start N2 purge and roof venting (-1) | Yes | Yes | Yes | 1.1.1.S1 CD-1 and HMI-1 concentration indication; 1.1.1.S2 operating check of PI-H2-1 | 4 | 2 | R2 | 1.1.1.R1 Confirm H2A-1 and EC-1 function as an independent tested protective function for high H2 isolation and purge | 1.1.1.CA Step 4 local cause and integrated worksheet basis applied ;
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.1 PV-H2-REG fails open or is set too high on the hydrogen feed to MG-100-2ME(Ex) | 1.1.2 Excess H2 feed can raise TK-500L pressure above the 10 bar design basis; fittings or nozzles may leak; released hydrogen can ignite as a jet fire | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.1.2.S1 Local pressure indication at PI-H2-1 and PI-OUT-1; 1.1.2.S2 receiver mechanical design rating | 4 | 1 | R1 | 1.1.2.R1 Provide or verify independent overpressure protection for TK-500L against H2 regulator failure | 1.1.2.CA Initial likelihood and IPL credit approach based on retrieved LOPA likelihood and credit guidance ;
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.1 PV-H2-REG fails open or is set too high on the hydrogen feed to MG-100-2ME(Ex) | 1.1.3 High H2 differential pressure at the mixer can drive hydrogen toward the nitrogen branch; flammable gas may enter N2 piping and create ignition risk during venting or maintenance | 3 | 1 | R2 | 1.1.3.1 CV-N2-IN backflow prevention on the nitrogen feed when maintained and proof checked (-1) | Yes | Yes | Yes | 1.1.3.S1 N2 feed pressure indication at PI-N2-1; 1.1.3.S2 nitrogen SDS backflow prevention practice | 3 | 2 | R2 | 1.1.3.R1 Verify CV-N2-IN design orientation tightness test interval and suitability for hydrogen backflow prevention | 1.1.3.CA Check valve IPL treatment follows retrieved low demand check valve criteria
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.1 PV-H2-REG fails open or is set too high on the hydrogen feed to MG-100-2ME(Ex) | 1.1.4 Excess hydrogen inventory discharged during venting can form a flammable plume at the roof outlet; ignition may expose personnel or equipment to flame radiation | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.4.S1 FA-1 installed on the vent line but function is not sufficiently defined for IPL credit; 1.1.4.S2 roof discharge elevation | 3 | 1 | R2 | 1.1.4.R1 Define FA-1 service as flame arresting or filtration duty and verify roof vent dispersion for hydrogen-rich discharge | 1.1.4.CA Relief and vent devices require defined design basis before IPL credit
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.1 PV-H2-REG fails open or is set too high on the hydrogen feed to MG-100-2ME(Ex) | 1.1.5 Downstream Process receives hydrogen-rich gas above specification; process equipment may enter an unsafe flammability envelope or suffer production upset | 3 | 1 | R2 | 1.1.5.1 H2A-1 high H2 detection with EC-1 outlet isolation at SV-21.1 (-1) | Yes | Yes | Yes | 1.1.5.S1 HMI-1 abnormal concentration display; 1.1.5.S2 procedural investigation after failed recovery | 3 | 2 | R2 | 1.1.5.R1 Establish downstream acceptance limits and alarm response time for high H2 concentration | 1.1.5.CA HAZOP workflow followed from node intent through causes consequences safeguards and recommendations
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.2 SV-H2-IN fails open or remains energized during a demand for reduced hydrogen feed | 1.2.1 Hydrogen continues flowing to the mixer during low demand; TK-500L pressure and H2 inventory increase; loss of containment can lead to fire or explosion | 4 | 1 | R1 | 1.2.1.1 EC-1 high H2 sequence closes SV-27 after unsuccessful recovery and stops the mixer (-1) | Yes | Yes | Yes | 1.2.1.S1 PI-H2-1 and PI-OUT-1 operator observation; 1.2.1.S2 MG-100-2ME(Ex) Ex-rated construction | 4 | 2 | R2 | 1.2.1.R1 Verify SV-H2-IN fail position and add independent closure feedback if not already provided | 1.2.1.CA Confirm solenoid valve dangerous failure is included in proof test scope
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.2 SV-H2-IN fails open or remains energized during a demand for reduced hydrogen feed | 1.2.2 Excess hydrogen can accumulate in the mixer outlet and receiver inlet line; a small leak from threaded or flanged joints may form a flammable cloud | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.2.S1 Ex-rated mixer package; 1.2.2.S2 routine leak check and ventilation around package | 3 | 1 | R2 | 1.2.2.R1 Specify hydrogen leak detection or ventilation basis around MG-100-2ME(Ex) and TK-500L inlet piping | 1.2.2.CA No IPL credit taken for general area practices without independence and auditability
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.2 SV-H2-IN fails open or remains energized during a demand for reduced hydrogen feed | 1.2.3 Normal outlet flow can carry elevated H2 concentration to the downstream Process before inventory is corrected; ignition at downstream users can cause a flash fire | 4 | 1 | R1 | 1.2.3.1 H2A-1 high H2 detection with EC-1 closure of SV-21.1 (-1) | Yes | Yes | Yes | 1.2.3.S1 CD-1 concentration display; 1.2.3.S2 downstream operating communication procedure | 4 | 2 | R2 | 1.2.3.R1 Validate analyzer response time against downstream residence time and outlet isolation closing time | 1.2.3.CA Analyzer and emergency isolation should be functionally tested as one protective loop
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.2 SV-H2-IN fails open or remains energized during a demand for reduced hydrogen feed | 1.2.4 N2 dilution capacity may be overwhelmed; mixed gas can remain within hydrogen flammable limits in the receiver and outlet header | 4 | 1 | R1 | 1.2.4.1 H2A-1 high H2 detection with EC-1 opening SV-21.3 and SV-21.2 for purge and roof venting (-1) | Yes | Yes | Yes | 1.2.4.S1 N2 emergency purge hardware; 1.2.4.S2 operator investigation after persistent high H2 | 4 | 2 | R2 | 1.2.4.R1 Verify N2 purge flow capacity and ten minute recovery basis for worst credible stuck-open H2 feed | 1.2.4.CA Confirm purge sizing includes PV-H2-REG and SV-H2-IN failures
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.2 SV-H2-IN fails open or remains energized during a demand for reduced hydrogen feed | 1.2.5 High hydrogen consumption can deplete the supply and destabilize the mixture; downstream production may be interrupted or placed off specification | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.5.S1 PI-H2-1 local pressure indication; 1.2.5.S2 HMI-1 operating status display | 2 | 1 | R2 | 1.2.5.R1 Add operating limits for abnormal H2 usage rate and define operator response to sustained high feed | 1.2.5.CA Production and asset consequence retained because the deviation is outside intended operation
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.3 PV-N2-REG fails open or is adjusted too high on the nitrogen feed or emergency purge branch | 1.3.1 Excess nitrogen flow can overpressure TK-500L or the receiver outlet header; gasket leakage can release pressurized H2/N2 gas | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.1.S1 PI-N2-1 and PI-OUT-1 local pressure indication; 1.3.1.S2 TK-500L 10 bar mechanical rating | 3 | 1 | R2 | 1.3.1.R1 Verify independent pressure relief or pressure trip coverage for nitrogen regulator failure | 1.3.1.CA Pressure indication alone is not credited as IPL without alarm and defined response
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.3 PV-N2-REG fails open or is adjusted too high on the nitrogen feed or emergency purge branch | 1.3.2 Nitrogen dilution can drive receiver H2 concentration below the required value; downstream process chemistry or heating duty may be upset | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.2.S1 H2A-1 concentration monitoring; 1.3.2.S2 CD-1 and HMI-1 display | 2 | 1 | R2 | 1.3.2.R1 Define low H2 concentration alarm limits and downstream response requirements | 1.3.2.CA H2A-1 low concentration action not credited because only high H2 emergency action is defined
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.3 PV-N2-REG fails open or is adjusted too high on the nitrogen feed or emergency purge branch | 1.3.3 High nitrogen flow to the roof vent during flushing can create an oxygen-deficient cloud near the discharge or maintenance access; personnel asphyxiation is possible | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.3.S1 Roof discharge routing; 1.3.3.S2 nitrogen SDS recognition as simple asphyxiant | 3 | 1 | R2 | 1.3.3.R1 Confirm vent termination location dispersion and access restrictions for nitrogen purge discharge | 1.3.3.CA Asphyxiation consequence retained for high N2 flow scenarios
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.3 PV-N2-REG fails open or is adjusted too high on the nitrogen feed or emergency purge branch | 1.3.4 Excess nitrogen backpressure can suppress normal hydrogen addition at MG-100-2ME(Ex); receiver composition may oscillate and repeatedly fall outside specification | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.4.S1 H2A-1 trend indication; 1.3.4.S2 local N2 and H2 pressure indicators | 2 | 1 | R2 | 1.3.4.R1 Add operating envelope checks for N2 to H2 pressure balance at mixer inlet | 1.3.4.CA No independent IPL identified for composition oscillation
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.3 PV-N2-REG fails open or is adjusted too high on the nitrogen feed or emergency purge branch | 1.3.5 Sustained high nitrogen velocity through F-N2 and the regulator assembly can damage internals or carry particulate into downstream valves; equipment impairment and outage may result | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.5.S1 Intake filter F-N2 less than or equal to 50 micron; 1.3.5.S2 routine maintenance of regulator assembly | 2 | 1 | R2 | 1.3.5.R1 Establish inspection criteria for F-N2 and PV-N2-REG following high flow events | 1.3.5.CA Maintenance practices are safeguards only and not likelihood reduction IPLs
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.4 SV-21.3 opens spuriously on the emergency nitrogen purge line | 1.4.1 Uncommanded nitrogen purge enters TK-500L and increases receiver pressure; mixed gas may leak from the outlet manifold and form a flammable or asphyxiating atmosphere | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.1.S1 CV-12.3 limits reverse flow into the N2 branch; 1.4.1.S2 PI-OUT-1 local pressure indication | 3 | 1 | R2 | 1.4.1.R1 Add command feedback and alarm for unintended SV-21.3 opening | 1.4.1.CA SV-21.3 is the initiating failed final element and is not credited as protection
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.4 SV-21.3 opens spuriously on the emergency nitrogen purge line | 1.4.2 Receiver contents become over-diluted with nitrogen; downstream Process receives low H2 gas and may trip or produce off-spec material | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.2.S1 H2A-1 composition monitoring; 1.4.2.S2 HMI-1 operator display | 2 | 1 | R2 | 1.4.2.R1 Configure low H2 alarm and operator response for unplanned purge dilution | 1.4.2.CA Low H2 monitoring is treated as safeguard until action and independence are defined
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.4 SV-21.3 opens spuriously on the emergency nitrogen purge line | 1.4.3 With SV-21.1 in normal service; purge nitrogen can flow directly to the downstream Process at excessive rate; asphyxiant gas release or process upset may occur downstream | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.3.S1 Normal outlet check valve CV-12.1; 1.4.3.S2 operator monitoring at CD-1 | 3 | 1 | R2 | 1.4.3.R1 Define interlock logic to prevent SV-21.3 opening unless outlet isolation and vent path status are confirmed | 1.4.3.CA CV-12.1 does not prevent forward excess purge flow to the Process
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.4 SV-21.3 opens spuriously on the emergency nitrogen purge line | 1.4.4 During vent or flush lineup; excessive nitrogen can sweep receiver gas to the roof at higher than intended rate; roof discharge may create flammable or oxygen-deficient exposure | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.4.S1 Roof vent routing through SV-21.2 CV-12.2 and FA-1; 1.4.4.S2 procedural control of flushing | 3 | 1 | R2 | 1.4.4.R1 Verify maximum purge flow and roof vent dispersion for stuck-open SV-21.3 | 1.4.4.CA Vent hardware is not credited without sizing and proof of no impediment
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.4 SV-21.3 opens spuriously on the emergency nitrogen purge line | 1.4.5 Rapid purge flow can create pressure transients across CV-12.3 and the receiver manifold; valve internals or tubing may be damaged and require shutdown repair | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.5.S1 Stainless steel schedule 10 piping note; 1.4.5.S2 local pressure checks | 2 | 1 | R2 | 1.4.5.R1 Evaluate surge and transient pressure for emergency N2 purge actuation | 1.4.5.CA Asset consequence remains credible for rapid gas flow transients
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.5 EC-1 or HMI-1 logic fault initiates an unintended emergency sequence that opens SV-21.3 and SV-21.2 while SV-27 remains open | 1.5.1 Unnecessary purge and venting can discharge a high flow of mixed H2/N2 gas to the roof; ignition of the hydrogen component can cause a flash fire | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.1.S1 FA-1 on vent line with undefined protective duty; 1.5.1.S2 roof discharge location | 3 | 1 | R2 | 1.5.1.R1 Add diagnostics and permissives to prevent false emergency venting and verify FA-1 protective function | 1.5.1.CA EC-1 is the initiating system fault and is not credited as an IPL
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.5 EC-1 or HMI-1 logic fault initiates an unintended emergency sequence that opens SV-21.3 and SV-21.2 while SV-27 remains open | 1.5.2 Normal receiver inventory can be diverted away from the downstream Process; production interruption and off-spec operation may occur | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.2.S1 CD-1 and HMI-1 status indication; 1.5.2.S2 operator investigation procedure | 2 | 1 | R2 | 1.5.2.R1 Require event logging and alarm annunciation for automatic emergency sequence initiation | 1.5.2.CA Consequence is primarily operability and asset related
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.5 EC-1 or HMI-1 logic fault initiates an unintended emergency sequence that opens SV-21.3 and SV-21.2 while SV-27 remains open | 1.5.3 Simultaneous mixer feed and emergency purge can create unstable receiver pressure and composition; repeated cycling may stress valves and create leakage points | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.3.S1 PI-OUT-1 local indication; 1.5.3.S2 programmed ten minute recovery and alarm philosophy | 3 | 1 | R2 | 1.5.3.R1 Perform logic cause and effect review for simultaneous SV-27 SV-21.2 and SV-21.3 states | 1.5.3.CA Programmed recovery sequence should be validated against all valve state combinations
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.5 EC-1 or HMI-1 logic fault initiates an unintended emergency sequence that opens SV-21.3 and SV-21.2 while SV-27 remains open | 1.5.4 Receiver gas may be emptied or rapidly depressured through the roof vent; air ingress after depressurization can create a flammable mixture when hydrogen feed resumes | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.4.S1 CV-12.2 on vent line; 1.5.4.S2 CV-12.1 on process outlet; 1.5.4.S3 operating procedure for restart after venting | 3 | 1 | R2 | 1.5.4.R1 Add restart purge and oxygen exclusion checks after any unintended receiver venting event | 1.5.4.CA Check valves are safeguards but not credited for eliminating post-vent restart hazard
H2/N2 Gas Mixing and Receiver Tank System from customer N2 and H2 supplies through MG-100-2ME(Ex) to TK-500L; downstream outlet; emergency N2 purge; roof vent | Filter and regulate N2 and H2 to about 8 bar; mix through MG-100-2ME(Ex); buffer in TK-500L rated 10 bar; deliver 4.5-5 bar mixed gas to Process; isolate purge and vent on abnormal H2 or pressure | Flow | More | 1. More Flow | 1.5 EC-1 or HMI-1 logic fault initiates an unintended emergency sequence that opens SV-21.3 and SV-21.2 while SV-27 remains open | 1.5.5 False emergency operation can mask a real high H2 event and delay diagnosis; prolonged unsafe composition may remain in the receiver or outlet header | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.5.S1 H2A-1 auto calibration; 1.5.5.S2 alarm and indication at CD-1 and HMI-1 | 4 | 1 | R1 | 1.5.5.R1 Separate diagnostic alarms from protective trip alarms and define operator response for false or repeated emergency sequences | 1.5.5.CA Final risk remains high because the initiating event defeats the normal emergency control layer
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.1 CV-12.1 on the normal Process outlet leaks or sticks open during higher downstream Process pressure | 1.1.1 Process gas can flow backward into TK-500L; receiver composition becomes uncontrolled; mixed gas supplied later may be outside the intended H2/N2 specification | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.1.S1 PI-OUT-1 local pressure indication; 1.1.1.S2 H2A-1 concentration display; 1.1.1.S3 operator investigation after abnormal analyzer trend | 2 | 1 | R2 | 1.1.1.R1 Define allowable downstream backpressure and add a documented reverse-flow response for abnormal PI-OUT-1 or H2A-1 readings | 1.1.1.A1 Cause screening and worksheet structure aligned with retrieved Step 4 and template guidance
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.1 CV-12.1 on the normal Process outlet leaks or sticks open during higher downstream Process pressure | 1.1.2 Backflow can pressurize TK-500L from the Process side; receiver pressure may exceed the intended outlet pressure range; gasket or small connection leakage of hydrogen-containing gas may occur | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.2.S1 TK-500L 10 bar design rating; 1.1.2.S2 PI-OUT-1 local indication; 1.1.2.S3 SV-21.1 emergency isolation not credited unless independent reverse-pressure trip is confirmed | 3 | 1 | R2 | 1.1.2.R1 Verify reverse-pressure relief or isolation basis for the normal outlet connection to the downstream Process | 1.1.2.A1 Initial likelihood and IPL treatment referenced to retrieved IEL and IPL credit guidance
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.1 CV-12.1 on the normal Process outlet leaks or sticks open during higher downstream Process pressure | 1.1.3 If air or oxygen-bearing Process gas returns into the hydrogen-containing receiver; a flammable mixture can form inside TK-500L or connected piping; ignition could cause vessel or line damage with personnel exposure | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.1.3.S1 MG-100-2ME(Ex) equipment rating; 1.1.3.S2 H2A-1 indicates hydrogen concentration only; 1.1.3.S3 Control & Display and HMI abnormal indication | 4 | 1 | R1 | 1.1.3.R1 Evaluate need for independent oxygen detection or reverse-flow interlock on the Process outlet when oxidizing gas backflow is credible | 1.1.3.A1 Final risk remains high because no independent effective and auditable IPL is confirmed
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.1 CV-12.1 on the normal Process outlet leaks or sticks open during higher downstream Process pressure | 1.1.4 Reverse flow can carry contaminants from the downstream Process into MG-100-2ME(Ex) through TK-500L; mixer internals and analyzer sample surfaces may be fouled; control reliability can degrade | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.4.S1 F-H2 and F-N2 upstream filters do not protect against downstream contamination; 1.1.4.S2 H2A-1 auto calibration trend monitoring | 3 | 1 | R2 | 1.1.4.R1 Add inspection and cleaning criteria for H2A-1 and MG-100-2ME(Ex) following any confirmed Process-side reverse-flow event | 1.1.4.A1 No credit taken for normal monitoring because it does not independently prevent reverse flow
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.1 CV-12.1 on the normal Process outlet leaks or sticks open during higher downstream Process pressure | 1.1.5 Backflow from the Process can prevent reliable isolation of off-spec receiver inventory; unsafe gas may be retained in the outlet header and later routed to users | 3 | 1 | R2 | 1.1.5.1 H2A-1 high H2 alarm with EC-1 closing SV-21.1 if independent and proof-tested (-1) | Yes | Yes | Yes | 1.1.5.S1 CV-12.1 installed for backflow prevention but not credited because it is the failed initiating device; 1.1.5.S2 operating procedure for failed recovery investigation | 3 | 2 | R2 | 1.1.5.R1 Confirm H2A-1; EC-1; and SV-21.1 independence from CV-12.1 failure and document proof-test interval | 1.1.5.A1 Alarm and IPL credit applied only where independence; effectiveness; and auditability can be demonstrated
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.2 CV-12.3 on the emergency N2 purge branch fails to seat and permits receiver gas to flow backward into the purge line | 1.2.1 Hydrogen-containing receiver gas can enter the emergency N2 purge line; the purge header may contain flammable gas when assumed to be nitrogen service | 3 | 1 | R2 | 1.2.1.1 Normally closed SV-21.3 as independent emergency N2 branch isolation if fail-closed and tested (-1); 1.2.1.2 CV-N2-IN upstream check valve if independent and maintained (-1) | Yes | Yes | Yes | 1.2.1.S1 PI-N2-1 local N2 pressure indication; 1.2.1.S2 H2A-1 receiver concentration monitoring | 3 | 3 | R3 | 1.2.1.R1 Verify SV-21.3 fail position; proof-test method; and CV-N2-IN maintenance basis for reverse-flow protection | 1.2.1.A1 Check valve IPL credit basis follows retrieved low-demand check valve guidance
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.2 CV-12.3 on the emergency N2 purge branch fails to seat and permits receiver gas to flow backward into the purge line | 1.2.2 Reverse flow can displace nitrogen in the emergency purge branch; the next emergency purge may initially push hydrogen-rich gas rather than inert gas into TK-500L; recovery of high H2 concentration can be delayed | 3 | 1 | R2 | 1.2.2.1 SV-21.3 closed-position isolation if independent from CV-12.3 and functionally tested (-1) | Yes | Yes | Yes | 1.2.2.S1 Emergency Control sequence opens N2 purge on high H2; 1.2.2.S2 PI-N2-1 operator observation | 3 | 2 | R2 | 1.2.2.R1 Add pre-purge verification or purge-line blowdown requirement before returning the system to normal after CV-12.3 leakage | 1.2.2.A1 Final likelihood reduced by one credited IPL in accordance with retrieved IPL credit practice
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.2 CV-12.3 on the emergency N2 purge branch fails to seat and permits receiver gas to flow backward into the purge line | 1.2.3 Hydrogen migration into the N2 supply interface can create a flammable mixture if air enters during maintenance or disconnection; ignition could cause localized flash fire or pressure burst | 4 | 1 | R1 | 1.2.3.1 Normally closed SV-21.3 branch isolation if proof-tested and independent (-1); 1.2.3.2 CV-N2-IN upstream check valve if maintained as separate backflow barrier (-1) | Yes | Yes | Yes | 1.2.3.S1 Nitrogen SDS backflow prevention expectation; 1.2.3.S2 customer-side N2 regulator assembly pressure indication | 4 | 3 | R2 | 1.2.3.R1 Establish lockout; venting; and gas-test steps for N2-line maintenance where hydrogen back-migration is possible | 1.2.3.A1 Severity reflects flammable hydrogen hazard at a utility interface
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.2 CV-12.3 on the emergency N2 purge branch fails to seat and permits receiver gas to flow backward into the purge line | 1.2.4 Reverse pressure from TK-500L can expose N2 regulator components to non-design composition; regulator performance may deteriorate and future purge flow may be unreliable | 2 | 1 | R2 | 1.2.4.1 SV-21.3 normally closed isolation if confirmed tight shutoff and tested (-1) | Yes | Yes | Yes | 1.2.4.S1 PV-N2-REG mechanical pressure regulation; 1.2.4.S2 PI-N2-1 local indication | 2 | 2 | R3 | 1.2.4.R1 Include reverse-flow contamination inspection of PV-N2-REG and F-N2 following any CV-12.3 leakage finding | 1.2.4.A1 Asset consequence dominates this pathway
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.2 CV-12.3 on the emergency N2 purge branch fails to seat and permits receiver gas to flow backward into the purge line | 1.2.5 Reverse flow can mask loss of effective N2 purge capacity; during high H2 concentration the receiver may not dilute as intended and flammable gas may continue to be vented to roof for an extended period | 3 | 1 | R2 | 1.2.5.1 H2A-1 high H2 emergency sequence with alarm after failed recovery if independent from CV-12.3 (-1) | Yes | Yes | Yes | 1.2.5.S1 EC-1 sequence opens SV-21.3 and SV-21.2; 1.2.5.S2 Control & Display shows persistent high H2 | 3 | 2 | R2 | 1.2.5.R1 Add an alarm or permissive based on verified N2 purge pressure or flow during emergency flushing | 1.2.5.A1 Existing recovery alarm is credited only as an independent alarmed operator response when response time is adequate
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.3 CV-H2-IN on the hydrogen feed fails open or leaks; allowing mixed gas or N2-rich gas to flow backward into the H2 supply branch during low H2 supply pressure | 1.3.1 Nitrogen-containing mixed gas can backflow into the H2 line; hydrogen feed composition and pressure become unstable; MG-100-2ME(Ex) may deliver off-ratio gas to TK-500L | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.1.S1 PI-H2-1 local pressure indication; 1.3.1.S2 H2A-1 receiver concentration monitoring; 1.3.1.S3 SV-H2-IN isolation not credited without independent trip confirmation | 2 | 1 | R2 | 1.3.1.R1 Define acceptable H2 supply pressure differential and add response criteria for suspected CV-H2-IN leakage | 1.3.1.A1 Cause is local and single initiating event consistent with Step 4 screening rules
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.3 CV-H2-IN on the hydrogen feed fails open or leaks; allowing mixed gas or N2-rich gas to flow backward into the H2 supply branch during low H2 supply pressure | 1.3.2 Backflow into the H2 regulator assembly can overpressure or contaminate customer-side H2 components; subsequent regulator malfunction can cause unstable hydrogen feed to the mixer | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.2.S1 PV-H2-REG pressure regulation; 1.3.2.S2 PI-H2-1; 1.3.2.S3 F-H2 intake filter does not prevent reverse gas migration | 3 | 1 | R2 | 1.3.2.R1 Confirm reverse-pressure rating and contamination tolerance of PV-H2-REG; F-H2; and connected H2 supply components | 1.3.2.A1 No IPL credit assigned to normal regulator function because it is not demonstrated as independent reverse-flow protection
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.3 CV-H2-IN on the hydrogen feed fails open or leaks; allowing mixed gas or N2-rich gas to flow backward into the H2 supply branch during low H2 supply pressure | 1.3.3 Reverse gas movement can carry oxygen-bearing contamination if the H2 supply branch is opened after backflow; a flammable mixture may be present in the H2 line; ignition could result in flash fire or line rupture | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.3.3.S1 Hydrogen service classification and Ex-rated mixer reduce ignition likelihood but are not credited as IPL; 1.3.3.S2 maintenance gas testing practice if present | 4 | 1 | R1 | 1.3.3.R1 Require positive isolation; depressurization; and gas testing before opening the H2 feed branch after suspected reverse flow | 1.3.3.A1 Hydrogen SDS hazard supports conservative severity for flammable reverse-flow contamination
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.3 CV-H2-IN on the hydrogen feed fails open or leaks; allowing mixed gas or N2-rich gas to flow backward into the H2 supply branch during low H2 supply pressure | 1.3.4 Reverse flow can interrupt stable H2 delivery to MG-100-2ME(Ex); receiver H2 concentration may fall below target; downstream Process quality or reaction control may be affected | 2 | 1 | R2 | 1.3.4.1 H2A-1 low or abnormal H2 concentration alarm with operator response if configured and proceduralized (-1) | Yes | Yes | Yes | 1.3.4.S1 Control & Display and HMI concentration trend; 1.3.4.S2 PI-H2-1 local pressure trend | 2 | 2 | R3 | 1.3.4.R1 Confirm whether H2A-1 has low-H2 alarm limits and written operator response for reverse-flow or loss-of-H2 scenarios | 1.3.4.A1 Alarm credit depends on clear alarm; timely response; training; and documentation per retrieved IPL guidance
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.3 CV-H2-IN on the hydrogen feed fails open or leaks; allowing mixed gas or N2-rich gas to flow backward into the H2 supply branch during low H2 supply pressure | 1.3.5 Backflow through the H2 branch can create pressure oscillation at the mixer inlet; repeated upset may damage mixer controls or seats; hydrogen-containing gas release may occur at fittings during subsequent operation | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.5.S1 MG-100-2ME(Ex) package mechanical integrity; 1.3.5.S2 PI-H2-1 observation; 1.3.5.S3 routine leak checks | 3 | 1 | R2 | 1.3.5.R1 Add periodic tightness testing for CV-H2-IN and verify mixer inlet reverse-flow tolerance | 1.3.5.A1 Mechanical integrity safeguards are not credited as IPL without defined test criteria and pass/fail records
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.4 CV-N2-IN on the nitrogen feed fails open or leaks; allowing H2-rich gas from the mixer header to migrate backward into the N2 supply branch | 1.4.1 Hydrogen-containing gas can contaminate the N2 feed line; a utility normally treated as inert may become flammable in sections of the customer-side N2 system | 4 | 1 | R1 | 1.4.1.1 SV-N2-IN closed isolation if independent and proof-tested for reverse-flow prevention (-1) | Yes | Yes | Yes | 1.4.1.S1 PI-N2-1 local pressure indication; 1.4.1.S2 N2 supply labeling and SDS backflow prevention expectation | 4 | 2 | R2 | 1.4.1.R1 Establish documented proof testing for SV-N2-IN tight shutoff or install a second independent backflow barrier on the N2 feed | 1.4.1.A1 Single check valve failure likelihood and IPL limits referenced to retrieved guidance
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.4 CV-N2-IN on the nitrogen feed fails open or leaks; allowing H2-rich gas from the mixer header to migrate backward into the N2 supply branch | 1.4.2 H2-rich gas can reach the N2 regulator and filter assembly; nitrogen purge effectiveness may be impaired because the purge source becomes contaminated with fuel gas | 3 | 1 | R2 | 1.4.2.1 SV-N2-IN tight shutoff if independent from CV-N2-IN and regularly tested (-1) | Yes | Yes | Yes | 1.4.2.S1 PV-N2-REG pressure control; 1.4.2.S2 F-N2 particulate filter; 1.4.2.S3 PI-N2-1 trend review | 3 | 2 | R2 | 1.4.2.R1 Add a purge-gas quality verification step before relying on emergency N2 purge after N2-side reverse-flow indication | 1.4.2.A1 Final risk remains tolerable with controls only if SV-N2-IN is validated as an IPL
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.4 CV-N2-IN on the nitrogen feed fails open or leaks; allowing H2-rich gas from the mixer header to migrate backward into the N2 supply branch | 1.4.3 During maintenance on the N2 branch; trapped hydrogen may mix with air; ignition could cause flash fire; personnel burns; or damage to the regulator station | 4 | 1 | R1 | 1.4.3.1 SV-N2-IN isolation if locked closed or automatically closed and proof-tested before maintenance (-1) | Yes | Yes | Yes | 1.4.3.S1 Maintenance permit controls; 1.4.3.S2 gas testing prior to opening nitrogen equipment; 1.4.3.S3 PI-N2-1 pressure check | 4 | 2 | R2 | 1.4.3.R1 Update nitrogen-line maintenance procedure to include hydrogen testing and positive isolation after reverse-flow suspicion | 1.4.3.A1 Human response safeguards are not credited unless procedural frequency and response basis are auditable
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.4 CV-N2-IN on the nitrogen feed fails open or leaks; allowing H2-rich gas from the mixer header to migrate backward into the N2 supply branch | 1.4.4 Reverse H2 migration can cause an unexpected high H2 concentration in MG-100-2ME(Ex) when N2 feed is re-established; TK-500L may receive over-rich gas and downstream flammability risk increases | 4 | 1 | R1 | 1.4.4.1 H2A-1 high-H2 emergency action closing SV-21.1; opening SV-21.3; and opening SV-21.2 if independent and proof-tested (-1) | Yes | Yes | Yes | 1.4.4.S1 Control & Display; 1.4.4.S2 HMI abnormal concentration trend; 1.4.4.S3 operator investigation if recovery fails after 10 minutes | 4 | 2 | R2 | 1.4.4.R1 Confirm the 9 percent H2 emergency sequence is classified; proof-tested; and independent from N2 feed reverse-flow faults | 1.4.4.A1 Emergency logic credit is limited to one likelihood step pending SIL or IPL verification
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.4 CV-N2-IN on the nitrogen feed fails open or leaks; allowing H2-rich gas from the mixer header to migrate backward into the N2 supply branch | 1.4.5 Backflow can reduce available nitrogen inventory for emergency flushing; delayed dilution may keep TK-500L above the intended H2 concentration for longer than the control sequence assumes | 3 | 1 | R2 | 1.4.5.1 H2A-1 persistent high-H2 alarm after failed recovery with trained operator response (-1) | Yes | Yes | Yes | 1.4.5.S1 EC-1 mixer stop and alarm after unsuccessful 10 minute recovery; 1.4.5.S2 PI-N2-1 local indication | 3 | 2 | R2 | 1.4.5.R1 Add direct N2 purge-flow or purge-pressure confirmation to the emergency sequence | 1.4.5.A1 Recommendation addresses the remaining gap between concentration detection and verified purge availability
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.5 CV-12.2 on the roof vent and flush path fails to prevent reverse flow; allowing air or roof-header gas ingress toward TK-500L when the vent path is open or receiver pressure is low | 1.5.1 Air ingress can enter the receiver vent manifold and TK-500L; hydrogen-containing gas can form a flammable mixture inside the receiver or outlet header | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.1.S1 FA-1 on roof vent path not credited because function and rating are not confirmed; 1.5.1.S2 SV-21.2 normally controls vent opening; 1.5.1.S3 H2A-1 does not measure oxygen | 4 | 1 | R1 | 1.5.1.R1 Confirm FA-1 service as flame arrestor or filter; add oxygen monitoring or a validated vacuum/backflow barrier if air ingress is credible | 1.5.1.A1 No IPL credit taken for FA-1 due unclear device function in the source topology
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.5 CV-12.2 on the roof vent and flush path fails to prevent reverse flow; allowing air or roof-header gas ingress toward TK-500L when the vent path is open or receiver pressure is low | 1.5.2 Reverse flow from the roof discharge can contaminate the receiver with moisture or particulates; analyzer readings may become unreliable and emergency flushing decisions may be delayed | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.2.S1 H2A-1 auto calibration; 1.5.2.S2 Control & Display diagnostic indication; 1.5.2.S3 vent path inspection | 3 | 1 | R2 | 1.5.2.R1 Specify FA-1 maintenance and H2A-1 calibration checks after any confirmed vent backflow event | 1.5.2.A1 Analyzer diagnostics are treated as safeguards rather than IPLs for this consequence
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.5 CV-12.2 on the roof vent and flush path fails to prevent reverse flow; allowing air or roof-header gas ingress toward TK-500L when the vent path is open or receiver pressure is low | 1.5.3 If ignition occurs at or near the roof discharge; flame can propagate toward hydrogen-containing vent gas; personnel near the roof outlet may be exposed to flash fire | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.3.S1 FA-1 may provide flame-arresting function but is not credited until design basis is verified; 1.5.3.S2 hazardous area controls near vent discharge | 4 | 1 | R1 | 1.5.3.R1 Verify roof vent dispersion; ignition-source control; and flame-arrestor design basis for hydrogen service | 1.5.3.A1 Relief or vent devices are credited only when effectiveness and maintenance basis are confirmed
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.5 CV-12.2 on the roof vent and flush path fails to prevent reverse flow; allowing air or roof-header gas ingress toward TK-500L when the vent path is open or receiver pressure is low | 1.5.4 Reverse flow through the vent line can reduce effective emergency flushing to roof; off-spec hydrogen-rich gas may remain in TK-500L and later be sent to the downstream Process | 3 | 1 | R2 | 1.5.4.1 H2A-1 high-H2 emergency sequence with SV-21.1 isolation and alarmed operator response if independent and tested (-1) | Yes | Yes | Yes | 1.5.4.S1 SV-21.2 opens for emergency venting; 1.5.4.S2 EC-1 closes SV-27 and stops mixer after failed recovery | 3 | 2 | R2 | 1.5.4.R1 Add a verified vent-flow indication or pressure confirmation to demonstrate effective roof flushing during emergency sequence | 1.5.4.A1 Credit is applied to outlet isolation and alarm response; not to the failed vent check valve
H2/N2 Gas Mixing and Receiver Tank System | Filtered and pressure-regulated H2 and N2 are mixed in MG-100-2ME(Ex); buffered in TK-500L at max 10 bar; supplied to Process at 4.5-5 bar; and protected by H2 analysis; outlet isolation; N2 purge; and roof vent flushing | Flow | Reverse | 1. Reverse Flow | 1.5 CV-12.2 on the roof vent and flush path fails to prevent reverse flow; allowing air or roof-header gas ingress toward TK-500L when the vent path is open or receiver pressure is low | 1.5.5 Air ingress can create cyclic oxidation and flammable pockets in the vent manifold; repeated emergency flushes can discharge variable H2/air mixtures at the roof outlet with asset and safety exposure | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.5.S1 SV-21.2 position control; 1.5.5.S2 operating decision on leaving SV-21.2 open to empty receiver; 1.5.5.S3 routine vent-line inspection | 4 | 1 | R1 | 1.5.5.R1 Prohibit leaving SV-21.2 open without engineering review; define vent purge closure criteria and post-flush gas testing | 1.5.5.A1 Final risk remains intolerable until vent backflow and air-ingress controls are verified
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.1 PV-H2-REG fails high and delivers excessive hydrogen pressure to MG-100-2ME(Ex) | 1.1.1 Receiver pressure rises above intended operating pressure; TK-500L or connected piping may fail with high-pressure hydrogen-containing gas release; ignition can produce jet fire or explosion | 5 | 1 | R1 | 1.1.1.1 H2A-1 high H2 emergency sequence through EC-1 opens SV-21.2 and stops MG-100-2ME(Ex) (-1) | Yes | Yes | Yes | 1.1.1.S1 PI-H2-1 and PI-OUT-1 local pressure indication; 1.1.1.S2 TK-500L 10 bar design rating; 1.1.1.S3 Ex-rated MG-100-2ME(Ex) | 5 | 2 | R1 | 1.1.1.R1 Verify maximum failed-open H2 regulator pressure against TK-500L and piping design pressure; confirm independent high-pressure protection or add relief protection | 1.1.1.CA Validate EC-1 action basis and proof-test interval for overpressure service
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.1 PV-H2-REG fails high and delivers excessive hydrogen pressure to MG-100-2ME(Ex) | 1.1.2 Excess pressure propagates through SV-27 into TK-500L and the normal outlet; downstream Process equipment can be overpressured and leak flammable mixed gas | 4 | 1 | R1 | 1.1.2.1 H2A-1 high H2 emergency sequence through EC-1 closes SV-21.1 and opens SV-21.2 (-1) | Yes | Yes | Yes | 1.1.2.S1 CV-12.1 check valve on normal outlet; 1.1.2.S2 Control & Display and HMI indication of analyzer status | 4 | 2 | R2 | 1.1.2.R1 Confirm downstream Process maximum allowable pressure and define the required shutdown action on high receiver pressure | 1.1.2.CA Treat downstream pressure protection as an interface requirement with the customer process
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.1 PV-H2-REG fails high and delivers excessive hydrogen pressure to MG-100-2ME(Ex) | 1.1.3 Gas mixer discharge pressure increases; MG-100-2ME(Ex) internals or flanged joints may be overstressed; hydrogen leakage can form a flammable cloud near electrical and instrumentation equipment | 4 | 1 | R1 | 1.1.3.1 H2A-1 high H2 emergency sequence through EC-1 stops MG-100-2ME(Ex) and initiates venting (-1) | Yes | Yes | Yes | 1.1.3.S1 Ex-rated mixer selection; 1.1.3.S2 Hydrogen service piping specified as stainless steel schedule 10 or equivalent | 4 | 2 | R2 | 1.1.3.R1 Obtain MG-100-2ME(Ex) pressure rating and confirm it exceeds credible regulator failure pressure | 1.1.3.CA Include mixer overpressure case in package vendor design review
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.1 PV-H2-REG fails high and delivers excessive hydrogen pressure to MG-100-2ME(Ex) | 1.1.4 High-pressure hydrogen-rich gas may be routed to the roof vent during recovery; an ignitable plume can form at the discharge point and create personnel exposure or equipment damage on ignition | 3 | 1 | R2 | 1.1.4.1 H2A-1 high H2 emergency sequence through EC-1 controls venting and stops the mixer (-1) | Yes | Yes | Yes | 1.1.4.S1 FA-1 inline vent protection device; 1.1.4.S2 Roof discharge location separates venting from occupied areas where properly designed | 3 | 2 | R2 | 1.1.4.R1 Confirm roof vent dispersion basis; ignition source control; and FA-1 functional intent for hydrogen service | 1.1.4.CA Verify vent outlet hazardous area classification and exclusion zone
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.1 PV-H2-REG fails high and delivers excessive hydrogen pressure to MG-100-2ME(Ex) | 1.1.5 Repeated high-pressure excursions can damage regulator seats; analyzer sample components; and valve trim; resulting in loss of production availability and increased maintenance exposure | 2 | 1 | R2 | 1.1.5.1 H2A-1 abnormal H2 alarm and EC-1 shutdown sequence (-1) | Yes | Yes | Yes | 1.1.5.S1 Local regulator pressure indication at PI-H2-1; 1.1.5.S2 Preventive maintenance on pressure regulation assembly | 2 | 2 | R3 | 1.1.5.R1 Add regulator proof-test and set-pressure verification to the maintenance plan | 1.1.5.CA Confirm spare regulator strategy and alarm response procedure
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.2 PV-N2-REG fails high and overpressures the nitrogen feed or emergency purge branch | 1.2.1 Excess nitrogen pressure enters the receiver purge header; TK-500L pressure can exceed the 10 bar rating with vessel or line rupture and release of pressurized gas | 4 | 1 | R1 | 1.2.1.1 EC-1 high-pressure emergency function opens SV-21.2 to roof and stops feed to the receiver where configured (-1) | Yes | Yes | Yes | 1.2.1.S1 PI-N2-1 local pressure indication; 1.2.1.S2 CV-12.3 purge backflow prevention; 1.2.1.S3 TK-500L 10 bar design rating | 4 | 2 | R2 | 1.2.1.R1 Confirm whether EC-1 has an independent high-pressure input and define the final elements for N2 overpressure isolation | 1.2.1.CA If no independent pressure trip exists then add a high-pressure alarm or SIF study item
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.2 PV-N2-REG fails high and overpressures the nitrogen feed or emergency purge branch | 1.2.2 Receiver pressure increases while mixed gas remains connected to the downstream Process; overpressure can damage downstream instruments or piping and release hydrogen-containing gas | 4 | 1 | R1 | 1.2.2.1 EC-1 high-pressure emergency function closes SV-21.1 and opens SV-21.2 where configured (-1) | Yes | Yes | Yes | 1.2.2.S1 CV-12.1 on normal outlet; 1.2.2.S2 PI-OUT-1 local indication near outlet header | 4 | 2 | R2 | 1.2.2.R1 Verify downstream Process isolation philosophy for high receiver pressure caused by nitrogen regulator failure | 1.2.2.CA Record the maximum N2 supply pressure in the design basis
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.2 PV-N2-REG fails high and overpressures the nitrogen feed or emergency purge branch | 1.2.3 Excess purge pressure may force rapid venting to roof; high nitrogen discharge can displace oxygen locally and create an asphyxiation hazard near the vent termination | 3 | 1 | R2 | 1.2.3.1 EC-1 high-pressure emergency function limits receiver feed and controls vent path where configured (-1) | Yes | Yes | Yes | 1.2.3.S1 Roof vent discharge elevation; 1.2.3.S2 Nitrogen SDS hazard communication; 1.2.3.S3 Local operating procedures for purge activities | 3 | 2 | R2 | 1.2.3.R1 Confirm roof vent discharge location prevents oxygen-deficient atmosphere at access platforms or air intakes | 1.2.3.CA Consider O2 deficiency signage or access restriction near roof vent if dispersion study requires it
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.2 PV-N2-REG fails high and overpressures the nitrogen feed or emergency purge branch | 1.2.4 High N2 pressure can drive reverse stress across H2 or mixer-side check valves; valve leakage may send pressurized mixed gas into the wrong branch and create flammable or asphyxiant exposure during maintenance | 3 | 1 | R2 | 1.2.4.1 EC-1 high-pressure emergency function isolates receiver outlet and initiates controlled venting (-1) | Yes | Yes | Yes | 1.2.4.S1 CV-N2-IN and CV-H2-IN check valves; 1.2.4.S2 Feed isolation valves SV-N2-IN and SV-H2-IN; 1.2.4.S3 Local pressure indicators | 3 | 2 | R2 | 1.2.4.R1 Verify check valve pressure ratings and leakage acceptance criteria for differential pressure created by failed N2 regulation | 1.2.4.CA Include cross-branch pressurization in commissioning leak tests
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.2 PV-N2-REG fails high and overpressures the nitrogen feed or emergency purge branch | 1.2.5 Excess N2 pressure can dilute product gas and force off-specification H2/N2 composition to the downstream Process; production upset and equipment trips may occur | 2 | 1 | R2 | 1.2.5.1 H2A-1 analyzer alarm with EC-1 emergency sequence for abnormal H2 concentration (-1) | Yes | Yes | Yes | 1.2.5.S1 Control & Display and HMI concentration indication; 1.2.5.S2 Operator investigation after failed recovery | 2 | 2 | R3 | 1.2.5.R1 Define off-spec gas diversion and restart criteria after N2 regulator failure | 1.2.5.CA Confirm analyzer response time is adequate for downstream Process protection
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.3 SV-21.1 or CV-12.1 closes or sticks shut while mixed gas feed continues to TK-500L | 1.3.1 Normal receiver outlet is blocked; continued feed from MG-100-2ME(Ex) raises TK-500L pressure and can result in receiver or outlet header failure with flammable gas release | 4 | 1 | R1 | 1.3.1.1 EC-1 high-pressure emergency function opens SV-21.2 to roof and stops MG-100-2ME(Ex) where configured (-1) | Yes | Yes | Yes | 1.3.1.S1 PI-OUT-1 local pressure indication; 1.3.1.S2 HMI and Control & Display abnormal condition indication | 4 | 2 | R2 | 1.3.1.R1 Confirm blocked-outlet overpressure case is covered by an independent pressure shutdown or relief basis | 1.3.1.CA Verify fail positions and diagnostic coverage for SV-21.1 and CV-12.1
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.3 SV-21.1 or CV-12.1 closes or sticks shut while mixed gas feed continues to TK-500L | 1.3.2 If pressure rises rapidly before venting is established; rupture of hydrogen-containing piping can form a flammable cloud; delayed ignition may cause explosion with multiple personnel exposure | 5 | 1 | R1 | 1.3.2.1 EC-1 high-pressure emergency function opens SV-21.2 and closes SV-27 or stops the mixer where configured (-1) | Yes | Yes | Yes | 1.3.2.S1 Stainless-steel schedule 10 piping specification; 1.3.2.S2 Ex-rated mixer selection; 1.3.2.S3 Local pressure monitoring | 5 | 2 | R1 | 1.3.2.R1 Perform LOPA for blocked normal outlet and determine whether a certified SIF or pressure relief device is required | 1.3.2.CA Final risk remains high without additional independent protection
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.3 SV-21.1 or CV-12.1 closes or sticks shut while mixed gas feed continues to TK-500L | 1.3.3 Downstream Process loses gas supply while receiver pressure increases; unstable operation or unplanned shutdown of downstream equipment may follow | 3 | 1 | R2 | 1.3.3.1 EC-1 high-pressure emergency function stops MG-100-2ME(Ex) and alarms the operator where configured (-1) | Yes | Yes | Yes | 1.3.3.S1 HMI alarm display; 1.3.3.S2 Operating procedure for investigation after unsuccessful recovery | 3 | 2 | R2 | 1.3.3.R1 Define operator response for simultaneous no-flow to process and high receiver pressure | 1.3.3.CA Coordinate alarm rationalization with downstream Process users
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.3 SV-21.1 or CV-12.1 closes or sticks shut while mixed gas feed continues to TK-500L | 1.3.4 Continued compression into a blocked receiver can overpressure the mixer discharge line through SV-27; flange leakage can release hydrogen-rich gas near the package | 4 | 1 | R1 | 1.3.4.1 EC-1 high-pressure emergency function closes SV-27 or stops MG-100-2ME(Ex) where configured (-1) | Yes | Yes | Yes | 1.3.4.S1 SV-27 on mixer outlet; 1.3.4.S2 PI-OUT-1 local pressure indication; 1.3.4.S3 Package leak checks during maintenance | 4 | 2 | R2 | 1.3.4.R1 Verify SV-27 is suitable as a final element for blocked receiver pressure protection if credited | 1.3.4.CA Include SV-27 stroke testing in proof-test program if used for protection
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.3 SV-21.1 or CV-12.1 closes or sticks shut while mixed gas feed continues to TK-500L | 1.3.5 Repeated blocked-outlet pressure cycling can damage SV-21.1 seats; CV-12.1 internals; and receiver outlet fittings; causing production downtime and maintenance exposure | 2 | 1 | R2 | 1.3.5.1 EC-1 high-pressure alarm and mixer stop where configured (-1) | Yes | Yes | Yes | 1.3.5.S1 Preventive maintenance for solenoid and check valves; 1.3.5.S2 Local pressure rounds | 2 | 2 | R3 | 1.3.5.R1 Establish valve functional test intervals for SV-21.1 and CV-12.1 | 1.3.5.CA Confirm spare valve availability for the receiver outlet assembly
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.4 Receiver vent path is obstructed by SV-21.2 failure closed; CV-12.2 stuck shut; FA-1 blockage; or MV-TK-VENT misposition | 1.4.1 Emergency out-breathing capacity is lost; continued feed or purge can raise TK-500L pressure toward mechanical failure and release hydrogen-containing gas | 4 | 2 | R2 | 1.4.1.1 EC-1 closes SV-27 and stops MG-100-2ME(Ex) after abnormal condition where configured (-1) | Yes | Yes | Yes | 1.4.1.S1 PI-OUT-1 local pressure indication; 1.4.1.S2 Roof vent line inspection; 1.4.1.S3 MV-TK-VENT normal-position control | 4 | 3 | R2 | 1.4.1.R1 Add proof testing or inspection for SV-21.2; CV-12.2; FA-1; and MV-TK-VENT position management | 1.4.1.CA Vent path blockage is a critical scenario for receiver overpressure
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.4 Receiver vent path is obstructed by SV-21.2 failure closed; CV-12.2 stuck shut; FA-1 blockage; or MV-TK-VENT misposition | 1.4.2 During high H2 recovery the receiver cannot discharge to roof; pressure and hydrogen concentration may remain high; subsequent leakage can ignite and cause explosion | 5 | 2 | R1 | 1.4.2.1 EC-1 closes SV-27 and stops MG-100-2ME(Ex) after failed recovery where configured (-1) | Yes | Yes | Yes | 1.4.2.S1 H2A-1 analyzer with auto calibration; 1.4.2.S2 Alarm after 10 min unsuccessful recovery; 1.4.2.S3 Operator investigation requirement | 5 | 3 | R1 | 1.4.2.R1 Provide independent confirmation of vent flow during emergency purge; consider vent-open proof or flow indication | 1.4.2.CA Final risk remains high because the primary disposal path is impaired
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.4 Receiver vent path is obstructed by SV-21.2 failure closed; CV-12.2 stuck shut; FA-1 blockage; or MV-TK-VENT misposition | 1.4.3 N2 purge flow may pressurize a blocked receiver instead of flushing it; nitrogen and hydrogen-containing gas can be forced through weak joints with local asphyxiation or flammable-gas exposure | 3 | 2 | R2 | 1.4.3.1 EC-1 stops MG-100-2ME(Ex) and alarms failed recovery after 10 min (-1) | Yes | Yes | Yes | 1.4.3.S1 CV-12.3 on N2 purge branch; 1.4.3.S2 HMI emergency sequence indication; 1.4.3.S3 Routine inspection of purge and vent valves | 3 | 3 | R3 | 1.4.3.R1 Review purge logic so N2 addition cannot continue against a confirmed blocked vent path | 1.4.3.CA Consider permissive requiring verified vent path before purge admission
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.4 Receiver vent path is obstructed by SV-21.2 failure closed; CV-12.2 stuck shut; FA-1 blockage; or MV-TK-VENT misposition | 1.4.4 Blocked vent prevents safe depressurization before maintenance or restart; trapped pressurized hydrogen-containing gas may be released when equipment is opened | 4 | 2 | R2 | No credited IPL identified | No | No | No | 1.4.4.S1 Lockout and depressurization procedure; 1.4.4.S2 Local pressure verification using PI-OUT-1; 1.4.4.S3 Gas testing before opening | 4 | 2 | R2 | 1.4.4.R1 Add a formal zero-energy and gas-free verification step for TK-500L and vent manifold maintenance | 1.4.4.CA Do not credit manual pressure checks unless procedure and independence are verified
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.4 Receiver vent path is obstructed by SV-21.2 failure closed; CV-12.2 stuck shut; FA-1 blockage; or MV-TK-VENT misposition | 1.4.5 Vent blockage can delay removal of off-spec gas; extended outage and repeated emergency cycling may damage solenoid valves and reduce system availability | 3 | 2 | R2 | No credited IPL identified | No | No | No | 1.4.5.S1 Preventive maintenance for FA-1 and vent valves; 1.4.5.S2 HMI failed-recovery alarm; 1.4.5.S3 Operator troubleshooting procedure | 3 | 2 | R2 | 1.4.5.R1 Define FA-1 inspection criteria and maximum allowable pressure drop for continued operation | 1.4.5.CA Track vent restriction as a safety-critical impairment
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.5 CV-12.1 leaks or fails open and allows higher-pressure downstream gas to backflow into TK-500L | 1.5.1 Reverse pressure from the downstream Process raises receiver pressure above the intended 4.5-5 bar outlet condition; TK-500L or outlet piping can leak hydrogen-containing gas | 4 | 1 | R1 | 1.5.1.1 EC-1 abnormal pressure or H2 action closes SV-21.1 to isolate the normal outlet (-1) | Yes | Yes | Yes | 1.5.1.S1 CV-12.1 backflow prevention design; 1.5.1.S2 PI-OUT-1 local indication; 1.5.1.S3 Downstream interface operating pressure control | 4 | 2 | R2 | 1.5.1.R1 Confirm downstream maximum pressure and require check valve leak testing for CV-12.1 | 1.5.1.CA Do not credit CV-12.1 because its failure is the initiating cause
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.5 CV-12.1 leaks or fails open and allows higher-pressure downstream gas to backflow into TK-500L | 1.5.2 Backflow can introduce unknown or oxygen-containing gas into a hydrogen mixture under pressure; an explosive mixture may form in TK-500L or the outlet header | 5 | 1 | R1 | 1.5.2.1 EC-1 abnormal H2 or pressure action closes SV-21.1 and initiates controlled venting (-1) | Yes | Yes | Yes | 1.5.2.S1 H2A-1 analyzer with auto calibration; 1.5.2.S2 CV-12.1 check valve; 1.5.2.S3 Operating interface procedure with downstream Process | 5 | 2 | R1 | 1.5.2.R1 Evaluate need for double block and bleed or dual check valves at the downstream interface | 1.5.2.CA Final risk remains high if oxygen ingress can occur from downstream Process
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.5 CV-12.1 leaks or fails open and allows higher-pressure downstream gas to backflow into TK-500L | 1.5.3 Reverse flow can push receiver gas toward the mixer and feed branches; N2 or H2 supply components may be exposed to pressure outside their intended direction of service | 3 | 1 | R2 | 1.5.3.1 EC-1 abnormal condition action closes SV-21.1 and stops MG-100-2ME(Ex) (-1) | Yes | Yes | Yes | 1.5.3.S1 CV-H2-IN and CV-N2-IN feed check valves; 1.5.3.S2 SV-H2-IN and SV-N2-IN isolation valves; 1.5.3.S3 Local pressure indicators on feed assemblies | 3 | 2 | R2 | 1.5.3.R1 Verify reverse-flow design pressure and check valve orientation for all feed branches | 1.5.3.CA Include reverse pressurization in pre-startup verification
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.5 CV-12.1 leaks or fails open and allows higher-pressure downstream gas to backflow into TK-500L | 1.5.4 Backflow through a leaking check valve can defeat emergency outlet isolation and keep the receiver pressurized during purge or venting; flammable gas may continue to discharge to roof | 4 | 1 | R1 | 1.5.4.1 EC-1 closes SV-21.1 and opens SV-21.2 for controlled venting (-1) | Yes | Yes | Yes | 1.5.4.S1 SV-21.1 normal outlet isolation valve; 1.5.4.S2 SV-21.2 roof vent valve; 1.5.4.S3 FA-1 vent-line protection device | 4 | 2 | R2 | 1.5.4.R1 Confirm SV-21.1 tight shutoff requirement and proof-test leakage acceptance for emergency isolation | 1.5.4.CA Define how operators verify isolation before leaving SV-21.2 open to empty receiver
H2/N2 Gas Mixing and Receiver Tank System with regulated H2 and N2 feeds; MG-100-2ME(Ex); TK-500L; process outlet; emergency purge and roof vent | Provide filtered and pressure-regulated H2/N2 mixed gas to downstream Process at 4.5-5 bar; buffer gas in TK-500L rated 10 bar; monitor H2 and execute emergency isolation purge and roof venting | Pressure | More | 1. High Pressure | 1.5 CV-12.1 leaks or fails open and allows higher-pressure downstream gas to backflow into TK-500L | 1.5.5 Sustained reverse pressure can contaminate receiver inventory and force shutdown for purging; production loss and maintenance exposure occur during depressurization and recommissioning | 2 | 1 | R2 | 1.5.5.1 EC-1 abnormal condition alarm with SV-21.1 isolation (-1) | Yes | Yes | Yes | 1.5.5.S1 HMI and Control & Display status indication; 1.5.5.S2 Operator investigation after failed recovery; 1.5.5.S3 Downstream interface operating procedure | 2 | 2 | R3 | 1.5.5.R1 Add acceptance criteria for restart after reverse-flow or contamination event | 1.5.5.CA Document responsibility split between package supplier and downstream Process owner
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.1 F-N2 becomes restricted or plugged on the nitrogen feed to the mixer and emergency purge branch | 1.1.1 Nitrogen feed pressure to MG-100-2ME(Ex) decreases; TK-500L cannot maintain the intended outlet pressure; downstream Process mixed gas supply is interrupted | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.1.S1 PI-N2-1 local pressure indication; 1.1.1.S2 PI-OUT-1 local receiver outlet pressure indication | 2 | 1 | R2 | 1.1.1.R1 Add a low-pressure alarm or transmitter on the regulated N2 feed or TK-500L outlet with defined operator response | 1.1.1.A1 Confirm F-N2 inspection and differential pressure monitoring basis for filtered gas service
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.1 F-N2 becomes restricted or plugged on the nitrogen feed to the mixer and emergency purge branch | 1.1.2 Reduced nitrogen dilution can increase hydrogen fraction in the mixed gas while receiver pressure is low; flammable hydrogen-rich gas may be delivered toward the Process | 4 | 1 | R1 | 1.1.2.1 H2A-1 high hydrogen detection with EC-1 action to close SV-21.1 and alarm and stop mixer after failed recovery (-1) | Yes | Yes | Yes | 1.1.2.S1 H2 Analyzer auto calibration; 1.1.2.S2 Control and Display indication; 1.1.2.S3 HMI-1 operator display | 4 | 2 | R2 | 1.1.2.R1 Verify the H2A-1 and EC-1 protective function proof-test interval and confirm independence from the N2 feed restriction scenario | 1.1.2.A1 Confirm the high hydrogen trip set point and the 10 minute recovery logic are acceptable for downstream flammability limits
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.1 F-N2 becomes restricted or plugged on the nitrogen feed to the mixer and emergency purge branch | 1.1.3 TK-500L pressure may fall below downstream Process pressure; reverse flow can contaminate the receiver and mixer with process gas or air; an abnormal flammable mixture can form | 3 | 1 | R2 | 1.1.3.1 CV-12.1 reverse-flow prevention on the Process outlet when clean low-demand service is verified (-1) | Yes | Yes | Yes | 1.1.3.S1 PI-OUT-1 local pressure indication; 1.1.3.S2 routine outlet check valve inspection | 3 | 2 | R2 | 1.1.3.R1 Confirm CV-12.1 service cleanliness and inspection interval before retaining IPL credit | 1.1.3.A1 Check whether downstream Process pressure can exceed the minimum credible receiver pressure
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.1 F-N2 becomes restricted or plugged on the nitrogen feed to the mixer and emergency purge branch | 1.1.4 Emergency purge capacity is reduced; a high hydrogen condition in TK-500L may not be diluted effectively; flammable inventory can remain in the receiver or be routed to the roof vent | 4 | 1 | R1 | 1.1.4.1 H2A-1 high hydrogen detection with EC-1 isolation and alarm action independent of the plugged N2 filter for outlet isolation (-1) | Yes | Yes | Yes | 1.1.4.S1 SV-21.3 emergency N2 valve; 1.1.4.S2 CV-12.3 N2 purge check valve; 1.1.4.S3 operator investigation after failed recovery | 4 | 2 | R2 | 1.1.4.R1 Provide low N2 purge pressure permissive or alarm to confirm purge availability before crediting the emergency sequence | 1.1.4.A1 The N2 purge action should not be credited for dilution when the initiating cause restricts N2 supply
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.1 F-N2 becomes restricted or plugged on the nitrogen feed to the mixer and emergency purge branch | 1.1.5 Mixer pressure and composition control become unstable; repeated pressure cycling can upset MG-100-2ME(Ex) and cause production loss or minor equipment damage | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.5.S1 Local feed pressure checks; 1.1.5.S2 operator monitoring of mixed gas supply stability | 2 | 1 | R2 | 1.1.5.R1 Define maintenance criteria for F-N2 plugging and establish an operating response for low regulated N2 pressure | 1.1.5.A1 Treat filter blockage as a credible single initiating event within the node boundary
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.2 PV-H2-REG fails closed or regulates the hydrogen feed below the required mixer inlet pressure | 1.2.1 Hydrogen feed pressure to MG-100-2ME(Ex) decreases; total mixed gas production falls; TK-500L pressure decays and downstream Process supply is lost | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.1.S1 PI-H2-1 local hydrogen pressure indication; 1.2.1.S2 PI-OUT-1 local receiver pressure indication | 2 | 1 | R2 | 1.2.1.R1 Add regulated H2 low-pressure alarm with response to isolate or place the Process in a safe state | 1.2.1.A1 Confirm PV-H2-REG maintenance and calibration program for flammable gas service
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.2 PV-H2-REG fails closed or regulates the hydrogen feed below the required mixer inlet pressure | 1.2.2 Hydrogen concentration in the receiver can fall below the specified mixed gas value; downstream Process chemistry or product quality may move outside safe operating limits | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.2.S1 H2A-1 concentration indication; 1.2.2.S2 Control and Display trend review; 1.2.2.S3 HMI-1 operator observation | 3 | 1 | R2 | 1.2.2.R1 Confirm whether H2A-1 has a validated low hydrogen alarm and operator action for downstream process protection | 1.2.2.A1 No low hydrogen trip is credited because the described emergency logic is based on high hydrogen concentration
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.2 PV-H2-REG fails closed or regulates the hydrogen feed below the required mixer inlet pressure | 1.2.3 The receiver loses its normal pressure buffer; downstream flow controllers or consuming equipment may trip on insufficient supply pressure; production interruption follows | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.3.S1 TK-500L buffer volume; 1.2.3.S2 local outlet pressure indication; 1.2.3.S3 downstream operating surveillance | 2 | 1 | R2 | 1.2.3.R1 Establish minimum receiver pressure operating limit and shutdown response for sustained low pressure | 1.2.3.A1 TK-500L volume provides hold-up but is not an auditable IPL for low pressure
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.2 PV-H2-REG fails closed or regulates the hydrogen feed below the required mixer inlet pressure | 1.2.4 Low pressure in the H2 feed line can permit N2 or mixed gas backflow toward the hydrogen supply header; hydrogen service contamination and abnormal mixture formation may occur | 3 | 1 | R2 | 1.2.4.1 CV-H2-IN backflow prevention when verified suitable for clean low-demand hydrogen service (-1) | Yes | Yes | Yes | 1.2.4.S1 PI-H2-1 local pressure indication; 1.2.4.S2 hydrogen feed line check valve inspection | 3 | 2 | R2 | 1.2.4.R1 Verify CV-H2-IN orientation and leak-tightness test frequency for H2 supply contamination prevention | 1.2.4.A1 Check valve IPL credit depends on clean service and auditable inspection
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.2 PV-H2-REG fails closed or regulates the hydrogen feed below the required mixer inlet pressure | 1.2.5 MG-100-2ME(Ex) may operate outside its intended inlet pressure envelope; gas ratio control deteriorates and mixer package reliability can be impaired | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.5.S1 Ex-rated mixer package selection; 1.2.5.S2 operator monitoring of feed pressure indicators | 2 | 1 | R2 | 1.2.5.R1 Obtain vendor minimum inlet pressure requirements for MG-100-2ME(Ex) and incorporate them into operating procedures | 1.2.5.A1 Vendor limits are needed to confirm whether the consequence remains operability only
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.3 SV-27 fails closed or becomes restricted on the mixed gas line from MG-100-2ME(Ex) to TK-500L | 1.3.1 TK-500L is isolated from the mixer while the Process continues to consume gas; receiver pressure falls below the normal 4.5-5 bar outlet range | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.1.S1 PI-OUT-1 local receiver outlet pressure indication; 1.3.1.S2 Control and Display operating status | 2 | 1 | R2 | 1.3.1.R1 Provide valve position feedback and low receiver pressure alarm for SV-27 closure or restriction | 1.3.1.A1 Confirm SV-27 fail position and diagnostic coverage
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.3 SV-27 fails closed or becomes restricted on the mixed gas line from MG-100-2ME(Ex) to TK-500L | 1.3.2 MG-100-2ME(Ex) can discharge against a restricted outlet while receiver pressure remains low; local mixed gas leakage at mixer connections can create a small flammable gas fire case | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.2.S1 Ex-rated mixer equipment; 1.3.2.S2 stainless steel schedule 10 piping; 1.3.2.S3 operator investigation following abnormal pressure | 3 | 1 | R2 | 1.3.2.R1 Verify mixer outlet blocked-flow protection and define maximum allowable discharge pressure | 1.3.2.A1 No relief or automatic blocked-discharge protection is visible in the provided node data
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.3 SV-27 fails closed or becomes restricted on the mixed gas line from MG-100-2ME(Ex) to TK-500L | 1.3.3 As TK-500L pressure decays below downstream pressure; reverse flow from the Process can enter the receiver outlet; contamination or air ingress may form a flammable mixture | 3 | 1 | R2 | 1.3.3.1 CV-12.1 reverse-flow prevention on the normal outlet when verified for low-demand clean gas service (-1) | Yes | Yes | Yes | 1.3.3.S1 local pressure indication at receiver outlet; 1.3.3.S2 normal outlet valve SV-21.1 isolation capability | 3 | 2 | R2 | 1.3.3.R1 Confirm CV-12.1 functional test interval and verify reverse pressure design case with the downstream Process owner | 1.3.3.A1 SV-21.1 is not credited separately unless it is independent and automatically actuated for this low-pressure scenario
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.3 SV-27 fails closed or becomes restricted on the mixed gas line from MG-100-2ME(Ex) to TK-500L | 1.3.4 During an emergency flush demand the receiver may have insufficient pressure to drive gas to the roof vent path; abnormal hydrogen can remain in TK-500L for an extended period | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.4.S1 H2A-1 concentration indication; 1.3.4.S2 EC-1 alarm after failed recovery; 1.3.4.S3 SV-21.2 vent valve | 3 | 1 | R2 | 1.3.4.R1 Review emergency flush hydraulics for the case where SV-27 is unavailable and receiver pressure is depleted | 1.3.4.A1 Emergency logic should include confirmation that venting and purge flow are actually established
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.3 SV-27 fails closed or becomes restricted on the mixed gas line from MG-100-2ME(Ex) to TK-500L | 1.3.5 Loss of receiver make-up removes pressure buffering; downstream Process pressure can swing rapidly and initiate an unplanned unit shutdown | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.5.S1 TK-500L buffer volume; 1.3.5.S2 operator monitoring of supply pressure | 2 | 1 | R2 | 1.3.5.R1 Include SV-27 failure in operating response procedures for low receiver pressure and downstream supply loss | 1.3.5.A1 Confirm whether downstream Process has its own low-supply-pressure trip and restart procedure
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.4 SV-21.2 fails open or leaks on the receiver vent and flush path to roof during normal operation | 1.4.1 Mixed gas is continuously vented from TK-500L to the roof; receiver pressure falls and the normal Process outlet cannot maintain 4.5-5 bar | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.1.S1 PI-OUT-1 local receiver pressure indication; 1.4.1.S2 roof vent path visibility during rounds | 2 | 1 | R2 | 1.4.1.R1 Add SV-21.2 closed-position feedback and low receiver pressure alarm to detect unintended venting | 1.4.1.A1 Confirm SV-21.2 leakage class and fail position
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.4 SV-21.2 fails open or leaks on the receiver vent and flush path to roof during normal operation | 1.4.2 Hydrogen-containing mixed gas is released to the roof vent continuously; poor dispersion or ignition at the discharge can cause a flammable gas fire or explosion exposure | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.4.2.S1 FA-1 inline vent device not credited because function is not confirmed; 1.4.2.S2 roof discharge location; 1.4.2.S3 H2 flammability awareness | 4 | 1 | R1 | 1.4.2.R1 Verify FA-1 function and roof vent dispersion design and consider independent indication or interlock for unintended SV-21.2 opening | 1.4.2.A1 Final risk remains high without a confirmed independent vent protection basis
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.4 SV-21.2 fails open or leaks on the receiver vent and flush path to roof during normal operation | 1.4.3 Open connection to the vent path can allow air ingress during pressure cycling or shutdown; hydrogen and air can mix inside TK-500L or the vent line and create explosion potential | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.4.3.S1 CV-12.2 vent path check valve not credited without functional basis; 1.4.3.S2 FA-1 not credited until identified; 1.4.3.S3 operating procedure for vent isolation | 4 | 1 | R1 | 1.4.3.R1 Confirm CV-12.2 and FA-1 design intent for air ingress and flame propagation prevention and assign inspection requirements | 1.4.3.A1 Consider oxygen ingress detection or nitrogen sweep requirements for vent-open operation
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.4 SV-21.2 fails open or leaks on the receiver vent and flush path to roof during normal operation | 1.4.4 Nitrogen or mixed gas can be discharged at elevated rate to the roof area; oxygen displacement near the discharge can expose personnel to asphyxiation hazard | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.4.S1 Roof vent elevation; 1.4.4.S2 nitrogen SDS hazard communication; 1.4.4.S3 access control by procedure | 3 | 1 | R2 | 1.4.4.R1 Review roof vent discharge location against personnel access and add warning or restricted access controls if needed | 1.4.4.A1 Nitrogen is a simple asphyxiant and roof work controls should address abnormal venting
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.4 SV-21.2 fails open or leaks on the receiver vent and flush path to roof during normal operation | 1.4.5 Receiver pressure control becomes unstable because gas inventory is lost through the vent; downstream supply pressure fluctuates and Process equipment may trip | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.5.S1 PI-OUT-1 local pressure indication; 1.4.5.S2 operator monitoring of abnormal vent noise or flow | 2 | 1 | R2 | 1.4.5.R1 Include unintended venting of SV-21.2 in troubleshooting procedure for low receiver pressure | 1.4.5.A1 Position indication would improve diagnostic speed for this failure mode
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.5 PS-1 electrical power supply is lost to HMI Programming and Emergency Control functions | 1.5.1 Control power loss interrupts automatic control of solenoid valves and mixer support functions; TK-500L pressure decays as downstream Process demand continues | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.1.S1 Local pressure indicators remain available only if visually checked; 1.5.1.S2 operator response to control power loss | 2 | 1 | R2 | 1.5.1.R1 Define fail-safe valve positions for loss of PS-1 and add alarmed UPS or power-health monitoring where required | 1.5.1.A1 Loss of power is treated as a single initiating event affecting control availability
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.5 PS-1 electrical power supply is lost to HMI Programming and Emergency Control functions | 1.5.2 Control and display functions are unavailable during pressure decay; delayed recognition can allow prolonged low pressure and reverse-flow exposure at the receiver outlet | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.2.S1 PI-OUT-1 local pressure indication; 1.5.2.S2 field operator rounds; 1.5.2.S3 CV-12.1 non-credited unless tested for this demand | 3 | 1 | R2 | 1.5.2.R1 Provide independent low receiver pressure alarm or hardwired indication that remains available on normal control power failure | 1.5.2.A1 Operator monitoring alone is not credited as an IPL without alarm and response basis
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.5 PS-1 electrical power supply is lost to HMI Programming and Emergency Control functions | 1.5.3 H2A-1 and EC-1 protective functions may be unavailable during low-pressure operation; an abnormal hydrogen concentration can go undetected and flammable gas may reach the Process | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.3.S1 H2 Analyzer with auto calibration not credited when de-energized; 1.5.3.S2 HMI-1 and CD-1 status indication before power loss | 4 | 1 | R1 | 1.5.3.R1 Provide backup power or fail-safe shutdown for H2A-1 and EC-1 protective functions during PS-1 loss | 1.5.3.A1 Do not credit the emergency sequence where the initiating cause disables the logic and indication
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.5 PS-1 electrical power supply is lost to HMI Programming and Emergency Control functions | 1.5.4 If de-energized valve positions are not fail-safe; SV-21.2 or SV-21.3 may create unintended venting or purge flow; hydrogen-containing gas can be discharged to the roof | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.4.S1 roof vent discharge path; 1.5.4.S2 FA-1 inline vent device not credited without confirmed function; 1.5.4.S3 operating procedure for power loss | 4 | 1 | R1 | 1.5.4.R1 Document fail positions for SV-21.1 SV-21.2 SV-21.3 and SV-27 and verify they place TK-500L in a safe depressurized or isolated state | 1.5.4.A1 Confirm whether solenoid valves fail closed fail open or fail last on loss of power
H2/N2 Gas Mixing and Receiver Tank System from filtered regulated N2 and H2 feeds through MG-100-2ME(Ex) and TK-500L to Process and roof vent | Provide filtered pressure regulated monitored H2/N2 mixed gas to TK-500L and supply Process at 4.5-5 bar while protecting abnormal H2 or pressure by isolation purge and roof venting | Pressure | Less | 1. Low Pressure | 1.5 PS-1 electrical power supply is lost to HMI Programming and Emergency Control functions | 1.5.5 The gas mixing package enters an uncontrolled shutdown; receiver pressure and gas composition become uncertain; restart can cause extended production outage and equipment troubleshooting exposure | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.5.S1 manual pressure checks; 1.5.5.S2 restart procedure; 1.5.5.S3 equipment Ex rating | 2 | 1 | R2 | 1.5.5.R1 Develop a written shutdown and restart procedure for PS-1 loss including purge verification and H2 concentration confirmation | 1.5.5.A1 Restart should require confirmed receiver pressure and confirmed H2 concentration before opening SV-21.1
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.1 PV-H2-REG fails open or regulates high; excessive H2 pressure produces rapid compression heating in MG-100-2ME(Ex) and TK-500L | 1.1.1 Receiver gas temperature rises; TK-500L pressure increases; mechanical overstress can release hydrogen-containing gas with jet fire or explosion potential | 4 | 1 | R1 | 1.1.1.1 H2A-1 high H2 detection with EC-1 isolation of SV-21.1 and purge/vent sequence through SV-21.3 and SV-21.2 (-1) | Yes | Yes | Yes | 1.1.1.S1 TK-500L 10 bar design rating; 1.1.1.S2 PI-OUT-1 local pressure indication; 1.1.1.S3 Ex-rated mixer construction | 4 | 2 | R2 | 1.1.1.R1 Verify high-pressure and high-temperature protection basis for TK-500L including relief or automatic isolation requirements | Action to confirm PV-H2-REG failure case is included in relief and functional safety review
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.1 PV-H2-REG fails open or regulates high; excessive H2 pressure produces rapid compression heating in MG-100-2ME(Ex) and TK-500L | 1.1.2 Hot hydrogen-rich gas can pass from TK-500L to the downstream Process; downstream equipment may receive gas within the flammable range and ignite if an ignition source is present | 4 | 1 | R1 | 1.1.2.1 H2A-1 high H2 detection with EC-1 closure of SV-21.1 to isolate the normal outlet (-1) | Yes | Yes | Yes | 1.1.2.S1 CV-12.1 limits reverse flow from the downstream Process; 1.1.2.S2 Control & Display and HMI indication of analyzer status | 4 | 2 | R2 | 1.1.2.R1 Confirm H2A-1 alarm and SV-21.1 closure response time is adequate for downstream isolation under regulator high-pass conditions | Action to define proof test interval for H2A-1 and SV-21.1 final element
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.1 PV-H2-REG fails open or regulates high; excessive H2 pressure produces rapid compression heating in MG-100-2ME(Ex) and TK-500L | 1.1.3 Elevated gas temperature at MG-100-2ME(Ex) can overheat local metallic surfaces; a small H2 leak at fittings could ignite and expose the mixer package | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.1.3.S1 MG-100-2ME(Ex) hazardous area equipment selection; 1.1.3.S2 Hydrogen service leak-tight construction; 1.1.3.S3 Routine inspection of H2 connections | 4 | 1 | R1 | 1.1.3.R1 Add a documented overtemperature detection or shutdown basis for the mixer package if not already provided | Action to verify Ex certification covers abnormal regulator high-pressure thermal cases
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.1 PV-H2-REG fails open or regulates high; excessive H2 pressure produces rapid compression heating in MG-100-2ME(Ex) and TK-500L | 1.1.4 Thermal expansion and increased gas density stress can exceed gasket or small-bore connection capability; localized hydrogen-containing gas release may form a flammable cloud | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.4.S1 Stainless-steel piping specification; 1.1.4.S2 Local pressure indication; 1.1.4.S3 Preventive maintenance on threaded and flanged joints | 3 | 1 | R2 | 1.1.4.R1 Confirm joint ratings and leak-test requirements for the maximum credible regulator outlet pressure and temperature | Action to include gasket and small-bore connection checks in mechanical integrity scope
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.1 PV-H2-REG fails open or regulates high; excessive H2 pressure produces rapid compression heating in MG-100-2ME(Ex) and TK-500L | 1.1.5 Hot hydrogen-containing gas routed to the roof vent can create a buoyant flammable plume; ignition at the discharge point may cause flash fire or flashback exposure | 4 | 1 | R1 | 1.1.5.1 FA-1 flame arresting function on the vent path when designed and maintained for hydrogen service (-1) | Yes | Yes | Yes | 1.1.5.S1 Roof discharge location; 1.1.5.S2 SV-21.2 vent routing during emergency sequence; 1.1.5.S3 CV-12.2 on vent line | 4 | 2 | R2 | 1.1.5.R1 Verify FA-1 type; hydrogen suitability; installation distance; inspection interval; and roof vent dispersion basis | Action to obtain FA-1 datasheet and maintenance procedure
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.2 PV-N2-REG fails open or regulates high; excessive N2 pressure enters the mixer or purge header and heats TK-500L by rapid compression | 1.2.1 High-temperature N2 admission raises TK-500L pressure; receiver overstress can release mixed gas and create personnel exposure to pressure blast and hydrogen fire | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.2.1.S1 TK-500L maximum pressure rating of 10 bar; 1.2.1.S2 PI-N2-1 and PI-OUT-1 local pressure indication; 1.2.1.S3 N2 intake filtration by F-N2 | 4 | 1 | R1 | 1.2.1.R1 Evaluate need for independent high-pressure trip or relief device on the receiver for N2 regulator high-pass failure | Action to add PV-N2-REG failure-open case to relief design register
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.2 PV-N2-REG fails open or regulates high; excessive N2 pressure enters the mixer or purge header and heats TK-500L by rapid compression | 1.2.2 Hot N2-rich gas can dilute the mixed gas below intended H2 content; downstream Process quality upset or unstable operation can cause asset loss and production interruption | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.2.S1 H2A-1 concentration monitoring; 1.2.2.S2 Control & Display indication; 1.2.2.S3 Operator process monitoring downstream | 2 | 1 | R2 | 1.2.2.R1 Define low-H2 or off-ratio alarm response if downstream equipment is sensitive to N2-rich hot gas | Action to confirm whether H2A-1 provides low concentration alarm and operator instruction
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.2 PV-N2-REG fails open or regulates high; excessive N2 pressure enters the mixer or purge header and heats TK-500L by rapid compression | 1.2.3 Heated nitrogen released through the roof vent during flushing can accumulate locally at low ventilation locations; oxygen displacement can expose personnel to asphyxiation hazard | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.3.S1 Roof vent elevation; 1.2.3.S2 Nitrogen SDS hazard communication; 1.2.3.S3 Operating procedure for purge discharge | 3 | 1 | R2 | 1.2.3.R1 Verify roof vent location; access restriction; and oxygen-deficiency warning requirements for N2 emergency purge discharge | Action to include N2 asphyxiation controls in operating procedure and training
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.2 PV-N2-REG fails open or regulates high; excessive N2 pressure enters the mixer or purge header and heats TK-500L by rapid compression | 1.2.4 High-temperature high-velocity N2 flow can damage CV-12.3 seating; purge backflow prevention may be impaired and future H2 migration into the N2 branch can form a flammable mixture | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.4.S1 CV-12.3 check valve on emergency N2 line; 1.2.4.S2 CV-N2-IN on N2 feed; 1.2.4.S3 PI-N2-1 local indication | 3 | 1 | R2 | 1.2.4.R1 Confirm CV-12.3 temperature and velocity rating for regulator high-pass flow and add inspection after abnormal purge events | Action to include check valve functional test after any high-pressure N2 incident
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.2 PV-N2-REG fails open or regulates high; excessive N2 pressure enters the mixer or purge header and heats TK-500L by rapid compression | 1.2.5 Rapid hot N2 admission can entrain hydrogen-rich gas from TK-500L to the downstream Process before composition stabilizes; downstream flammable mixture exposure may occur | 4 | 1 | R1 | 1.2.5.1 H2A-1 high H2 detection with EC-1 closure of SV-21.1 and opening of SV-21.2 to divert gas to roof (-1) | Yes | Yes | Yes | 1.2.5.S1 CV-12.1 on normal outlet; 1.2.5.S2 HMI-1 emergency status indication; 1.2.5.S3 Operator investigation after failed recovery | 4 | 2 | R2 | 1.2.5.R1 Confirm emergency logic addresses N2 regulator high-pass and hot gas displacement scenarios | Action to test EC-1 sequence under simulated high H2 and purge flow demand
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.3 MG-100-2ME(Ex) develops an internal mechanical or electrical overheating fault; heat is transferred directly to the mixed H2/N2 stream | 1.3.1 Hot mixed gas enters TK-500L; receiver contents can reach ignition-supporting conditions and deflagration may occur if air ingress or an ignition source is present | 4 | 2 | R2 | No credited IPL identified | No | No | No | 1.3.1.S1 Ex-rated MG-100-2ME(Ex); 1.3.1.S2 H2 service equipment selection; 1.3.1.S3 H2A-1 concentration monitoring | 4 | 2 | R2 | 1.3.1.R1 Provide independent mixer overtemperature alarm or shutdown where supplier data show credible heat generation into the gas stream | Action to request mixer vendor abnormal heat generation and trip philosophy information
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.3 MG-100-2ME(Ex) develops an internal mechanical or electrical overheating fault; heat is transferred directly to the mixed H2/N2 stream | 1.3.2 Overheated mixer surfaces can ignite a minor H2 leak from the regulated H2 feed or mixer connections; local jet fire can damage adjacent valves and instrumentation | 4 | 2 | R2 | No credited IPL identified | No | No | No | 1.3.2.S1 Hazardous area equipment certification; 1.3.2.S2 Hydrogen leak-tight installation practices; 1.3.2.S3 Local inspection and maintenance program | 4 | 2 | R2 | 1.3.2.R1 Confirm surface temperature class and abnormal fault temperature margin for MG-100-2ME(Ex) in hydrogen service | Action to document Ex inspection frequency for the mixer and nearby solenoid valves
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.3 MG-100-2ME(Ex) develops an internal mechanical or electrical overheating fault; heat is transferred directly to the mixed H2/N2 stream | 1.3.3 Prolonged elevated temperature can degrade elastomeric seals or gaskets in the mixer outlet piping; hydrogen-containing gas leakage can create a localized flash fire | 3 | 2 | R2 | No credited IPL identified | No | No | No | 1.3.3.S1 Stainless-steel schedule 10 piping; 1.3.3.S2 Preventive maintenance on seals and fittings; 1.3.3.S3 Operator rounds for abnormal noise or odorless gas release indications | 3 | 2 | R2 | 1.3.3.R1 Verify seal and gasket material compatibility with maximum credible mixer fault temperature | Action to add mixer outlet leak check after overheating alarm or trip
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.3 MG-100-2ME(Ex) develops an internal mechanical or electrical overheating fault; heat is transferred directly to the mixed H2/N2 stream | 1.3.4 Hot mixed gas delivered at the normal outlet can exceed downstream Process inlet temperature tolerance; downstream equipment damage or unsafe reaction behavior may result | 3 | 2 | R2 | No credited IPL identified | No | No | No | 1.3.4.S1 Downstream process monitoring outside this node; 1.3.4.S2 HMI-1 operating status display; 1.3.4.S3 SV-21.1 normal outlet isolation capability | 3 | 2 | R2 | 1.3.4.R1 Confirm downstream allowable inlet temperature and add outlet temperature indication if the margin is insufficient | Action to obtain downstream Process temperature design limits
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.3 MG-100-2ME(Ex) develops an internal mechanical or electrical overheating fault; heat is transferred directly to the mixed H2/N2 stream | 1.3.5 Mixer overheating can lead to automatic or manual shutdown after equipment distress; mixed gas supply to the downstream Process is interrupted and production loss can occur | 2 | 2 | R3 | No credited IPL identified | No | No | No | 1.3.5.S1 Control & Display indication; 1.3.5.S2 Operator investigation procedure; 1.3.5.S3 Receiver buffer volume in TK-500L | 2 | 2 | R3 | 1.3.5.R1 Define restart and investigation criteria following mixer overheating or abnormal temperature indication | Action to include mixer overheating in operating and maintenance troubleshooting guide
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.4 SV-21.3 opens spuriously during normal operation; excessive emergency N2 enters the receiver purge header and heats gas by rapid compression | 1.4.1 Rapid N2 inflow compresses gas in TK-500L; receiver pressure and temperature rise; mechanical failure can release H2/N2 gas with fire and blast exposure | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.4.1.S1 TK-500L 10 bar rating; 1.4.1.S2 CV-12.3 check valve on emergency line; 1.4.1.S3 PI-OUT-1 local pressure indication | 4 | 1 | R1 | 1.4.1.R1 Add independent high-pressure protection or confirm relief capacity for spurious SV-21.3 opening during normal receiver filling | Action to verify SV-21.3 fail position and proof-test records
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.4 SV-21.3 opens spuriously during normal operation; excessive emergency N2 enters the receiver purge header and heats gas by rapid compression | 1.4.2 Hot N2-rich gas can be delivered to the downstream Process through SV-21.1; product composition and temperature deviations may cause process upset and equipment damage | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.2.S1 H2A-1 concentration indication; 1.4.2.S2 HMI display of emergency valve status; 1.4.2.S3 Downstream operator monitoring | 3 | 1 | R2 | 1.4.2.R1 Provide alarm for unexpected SV-21.3 open status during normal operation | Action to configure HMI permissive or annunciation for emergency N2 valve position
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.4 SV-21.3 opens spuriously during normal operation; excessive emergency N2 enters the receiver purge header and heats gas by rapid compression | 1.4.3 Turbulent hot purge inflow can carry hydrogen-containing gas toward the vent manifold; if the vent path is open the roof discharge may form a flammable or oxygen-deficient plume | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.3.S1 SV-21.2 normally controls vent opening; 1.4.3.S2 CV-12.2 on vent path; 1.4.3.S3 Roof discharge routing | 3 | 1 | R2 | 1.4.3.R1 Confirm interlock logic prevents unintended simultaneous purge and vent discharge unless in controlled emergency flush mode | Action to review EC-1 valve sequencing and permissives
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.4 SV-21.3 opens spuriously during normal operation; excessive emergency N2 enters the receiver purge header and heats gas by rapid compression | 1.4.4 High-temperature flow across CV-12.3 can damage the seat; reverse migration of hydrogen into the N2 branch can later produce a flammable mixture in piping intended for nitrogen service | 3 | 1 | R2 | 1.4.4.1 CV-N2-IN backflow prevention on the nitrogen feed when maintained and tested for low-demand reverse-flow service (-1) | Yes | Yes | Yes | 1.4.4.S1 CV-12.3 on the emergency N2 line; 1.4.4.S2 Nitrogen SDS backflow prevention requirement; 1.4.4.S3 PI-N2-1 local indication | 3 | 2 | R2 | 1.4.4.R1 Establish check valve inspection and reverse-flow test acceptance criteria for CV-12.3 and CV-N2-IN | Action to verify check valve credit basis and maintenance records
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.4 SV-21.3 opens spuriously during normal operation; excessive emergency N2 enters the receiver purge header and heats gas by rapid compression | 1.4.5 Continued hot N2 addition can displace breathable air at any vented or downstream release location; personnel exposure to oxygen-deficient atmosphere can cause serious injury | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.5.S1 Roof discharge location; 1.4.5.S2 Nitrogen hazard labeling; 1.4.5.S3 Operating procedure for emergency purge | 3 | 1 | R2 | 1.4.5.R1 Assess need for oxygen-deficiency monitoring or access restriction around vent discharge and downstream purge release points | Action to include spurious N2 purge in site emergency response drills
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.5 SV-21.1 fails closed on the normal receiver outlet while MG-100-2ME(Ex) continues feeding TK-500L; gas compression increases receiver temperature | 1.5.1 Continued mixer feed into a blocked normal outlet heats and pressurizes TK-500L; receiver failure can release hydrogen-containing gas and cause flash fire or explosion | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.1.S1 TK-500L 10 bar design rating; 1.5.1.S2 PI-OUT-1 local pressure indication; 1.5.1.S3 SV-27 can isolate mixer outlet when commanded by emergency logic | 4 | 1 | R1 | 1.5.1.R1 Provide independent high-pressure shutdown of MG-100-2ME(Ex) or relief protection for blocked outlet operation | Action to verify blocked outlet is addressed in operating envelope and relief review
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.5 SV-21.1 fails closed on the normal receiver outlet while MG-100-2ME(Ex) continues feeding TK-500L; gas compression increases receiver temperature | 1.5.2 Downstream Process supply is lost while hot gas accumulates in TK-500L; production interruption and downstream instability can occur | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.2.S1 Receiver buffer volume; 1.5.2.S2 HMI-1 valve status indication; 1.5.2.S3 Downstream process monitoring | 2 | 1 | R2 | 1.5.2.R1 Add clear alarm and operating instruction for unexpected closure of SV-21.1 during normal supply mode | Action to confirm SV-21.1 position feedback is displayed to operators
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.5 SV-21.1 fails closed on the normal receiver outlet while MG-100-2ME(Ex) continues feeding TK-500L; gas compression increases receiver temperature | 1.5.3 Hot stagnant hydrogen-containing gas in the receiver outlet manifold can increase leakage through small fittings; a localized flammable cloud can form near the valve manifold | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.3.S1 Stainless-steel outlet manifold; 1.5.3.S2 Routine leak inspection; 1.5.3.S3 Hydrogen hazard awareness for invisible flame | 3 | 1 | R2 | 1.5.3.R1 Include receiver outlet manifold leak testing after blocked outlet or high-temperature events | Action to update maintenance checklist for SV-21.1 and CV-12.1 manifold
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.5 SV-21.1 fails closed on the normal receiver outlet while MG-100-2ME(Ex) continues feeding TK-500L; gas compression increases receiver temperature | 1.5.4 Backpressure from TK-500L can heat the mixer discharge line and overload MG-100-2ME(Ex); mixer damage may release hydrogen-containing gas inside the package boundary | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.4.S1 SV-27 on mixer outlet; 1.5.4.S2 Ex-rated mixer package; 1.5.4.S3 Control and Display operating indication | 3 | 1 | R2 | 1.5.4.R1 Confirm MG-100-2ME(Ex) has high-discharge-pressure or high-temperature shutdown for blocked receiver outlet | Action to obtain vendor protection details for mixer backpressure operation
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated N2 and H2 are mixed; buffered in TK-500L up to 10 bar; delivered at 4.5-5 bar; abnormal H2 is isolated; purged with N2; vented to roof | Temperature | More | 1. High Temperature | 1.5 SV-21.1 fails closed on the normal receiver outlet while MG-100-2ME(Ex) continues feeding TK-500L; gas compression increases receiver temperature | 1.5.5 If heated receiver gas is diverted to the roof vent to control inventory; a hot hydrogen-containing plume can ignite and expose roof equipment and personnel | 4 | 1 | R1 | 1.5.5.1 FA-1 flame arresting function on the roof vent line when specified for hydrogen service and maintained (-1) | Yes | Yes | Yes | 1.5.5.S1 SV-21.2 emergency vent valve; 1.5.5.S2 CV-12.2 vent check valve; 1.5.5.S3 Roof discharge endpoint | 4 | 2 | R2 | 1.5.5.R1 Validate roof vent dispersion; radiation exposure; and FA-1 suitability for blocked outlet emergency venting | Action to document whether venting heated H2/N2 is an approved response to SV-21.1 failed-closed operation
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.1 PV-H2-REG malfunctions with excessive pressure reduction across the hydrogen feed to MG-100-2ME(Ex) | 1.1.1 Hydrogen feed temperature falls below the intended operating envelope; regulator or filter icing can further reduce H2 delivery; downstream mixed gas may become compositionally off specification | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.1.S1 PI-H2-1 local pressure indication; 1.1.1.S2 H2A-1 concentration monitoring without confirmed low-temperature compensation credit | 2 | 1 | R2 | 1.1.1.R1 Define minimum allowable H2 feed temperature and verify regulator anti-icing provisions | 1.1.1 Action to confirm cold-gas operating basis for PV-H2-REG and F-H2
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.1 PV-H2-REG malfunctions with excessive pressure reduction across the hydrogen feed to MG-100-2ME(Ex) | 1.1.2 Excessively cold hydrogen chills the mixer inlet and adjacent 1 inch S316L piping; thermal contraction or seal hardening can produce hydrogen leakage; ignition may result in a local jet fire | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.1.2.S1 Ex-rated MG-100-2ME(Ex) equipment selection; 1.1.2.S2 routine leak checks and maintenance inspection | 4 | 1 | R1 | 1.1.2.R1 Verify minimum design temperature and elastomer compatibility for H2 service from PV-H2-REG through MG-100-2ME(Ex) | 1.1.2 Mechanical integrity basis is required before accepting low-temperature hydrogen operation
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.1 PV-H2-REG malfunctions with excessive pressure reduction across the hydrogen feed to MG-100-2ME(Ex) | 1.1.3 Cold hydrogen entering MG-100-2ME(Ex) can destabilize mixing performance; hydrogen-rich slugs may enter TK-500L and proceed toward the process at flammable concentration | 4 | 1 | R1 | 1.1.3.1 H2A-1 high H2 detection with EC-1 closure of SV-21.1 and initiation of purge vent sequence (-1) | Yes | Yes | Yes | 1.1.3.S1 CD-1 and HMI-1 operator indication; 1.1.3.S2 downstream CV-12.1 backflow prevention | 4 | 2 | R2 | 1.1.3.R1 Confirm H2A-1 and EC-1 independence from PV-H2-REG failure and define proof-test interval | 1.1.3 Credited protection depends on verified analyzer response at the expected cold-gas condition
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.1 PV-H2-REG malfunctions with excessive pressure reduction across the hydrogen feed to MG-100-2ME(Ex) | 1.1.4 Low-temperature gas contraction reduces TK-500L pressure and available outlet flow; the downstream process may lose the specified 4.5-5 bar mixed-gas supply and trip | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.4.S1 PI-OUT-1 local pressure indication; 1.1.4.S2 operator monitoring through Control and Display | 2 | 1 | R2 | 1.1.4.R1 Add alarmed low receiver pressure or low outlet pressure response criteria if process continuity is safety or asset critical | 1.1.4 Consequence is primarily operability and production unless downstream hazard is confirmed
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.1 PV-H2-REG malfunctions with excessive pressure reduction across the hydrogen feed to MG-100-2ME(Ex) | 1.1.5 Cold hydrogen exposure can drive H2A-1 sample or sensor conditions outside validated compensation range; hydrogen concentration may be under-reported and unsafe gas may remain aligned to the process | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.1.5.S1 H2 Analyzer with Auto Calibration; 1.1.5.S2 CD-1 and HMI-1 displayed concentration trend | 4 | 1 | R1 | 1.1.5.R1 Verify H2A-1 low-temperature accuracy envelope and add independent validation or sample conditioning if required | 1.1.5 H2A-1 is not credited where the same cold condition can impair the analyzer measurement
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.2 PV-N2-REG malfunctions with excessive pressure reduction across the nitrogen feed and emergency purge branch | 1.2.1 Nitrogen feed temperature and pressure fall below the mixing requirement; dilution is reduced and hydrogen concentration in TK-500L can rise toward a flammable off-specification condition | 4 | 1 | R1 | 1.2.1.1 H2A-1 high H2 detection with EC-1 closure of SV-21.1 and opening of SV-21.2 and SV-21.3 (-1) | Yes | Yes | Yes | 1.2.1.S1 PI-N2-1 local pressure indication; 1.2.1.S2 operator monitoring at CD-1 and HMI-1 | 4 | 2 | R2 | 1.2.1.R1 Confirm EC-1 emergency sequence is functionally tested for low N2 temperature and low N2 pressure initiating conditions | 1.2.1 Credited IPL requires demonstrated analyzer and valve response before process exposure
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.2 PV-N2-REG malfunctions with excessive pressure reduction across the nitrogen feed and emergency purge branch | 1.2.2 Cold nitrogen can ice F-N2 or the N2 emergency purge line; purge capacity through SV-21.3 and CV-12.3 may be insufficient to dilute and flush an abnormal receiver inventory | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.2.S1 PI-N2-1 local indication; 1.2.2.S2 emergency purge line design using 1 inch S316L schedule 10 or equivalent | 3 | 1 | R2 | 1.2.2.R1 Establish N2 dryness and filter inspection requirements to prevent cold-service icing in F-N2 and purge piping | 1.2.2 Purge impairment is treated as a consequence of the low-temperature N2 condition
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.2 PV-N2-REG malfunctions with excessive pressure reduction across the nitrogen feed and emergency purge branch | 1.2.3 Low-temperature nitrogen can chill SV-21.3 and CV-12.3; valve seat shrinkage or delayed reseating may allow unintended nitrogen leakage into the receiver outlet header | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.3.S1 CV-12.3 backflow prevention; 1.2.3.S2 local pressure indication at PI-OUT-1 | 3 | 1 | R2 | 1.2.3.R1 Confirm valve trim and seat materials for low-temperature nitrogen expansion service | 1.2.3 CV-12.3 is retained as a safeguard only because no proof-test or leakage performance basis is defined
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.2 PV-N2-REG malfunctions with excessive pressure reduction across the nitrogen feed and emergency purge branch | 1.2.4 Cold low-pressure nitrogen reduces receiver temperature and inventory pressure; downstream process supply may become unstable and cause an unplanned process shutdown | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.4.S1 TK-500L buffer volume; 1.2.4.S2 PI-OUT-1 pressure indication | 2 | 1 | R2 | 1.2.4.R1 Define alarm setpoints and operator response for low receiver pressure following N2 regulator malfunction | 1.2.4 Production impact should be reviewed with downstream process owner
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.2 PV-N2-REG malfunctions with excessive pressure reduction across the nitrogen feed and emergency purge branch | 1.2.5 Cold nitrogen can reduce H2A-1 sample temperature and create analyzer lag or calibration bias; abnormal hydrogen concentration may be detected late during receiver filling | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.2.5.S1 H2A-1 auto calibration; 1.2.5.S2 HMI-1 concentration trend review | 4 | 1 | R1 | 1.2.5.R1 Verify analyzer sample conditioning and cold-temperature response time for nitrogen regulator failure cases | 1.2.5 Analyzer is not credited when low temperature may degrade measurement reliability
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.3 SV-21.2 fails open or leaks on the receiver vent line to roof causing continuous expansion cooling of TK-500L contents | 1.3.1 Continuous receiver blowdown through the roof vent cools TK-500L and lowers outlet pressure; downstream process gas supply can be interrupted without controlled shutdown | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.1.S1 PI-OUT-1 local pressure indication; 1.3.1.S2 CD-1 and HMI-1 operator awareness of abnormal receiver condition | 2 | 1 | R2 | 1.3.1.R1 Add alarmed low receiver pressure and abnormal vent-flow response if not already provided | 1.3.1 Scenario assumes SV-21.2 leakage is sufficient to depressurize and cool the receiver
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.3 SV-21.2 fails open or leaks on the receiver vent line to roof causing continuous expansion cooling of TK-500L contents | 1.3.2 Hydrogen-containing gas is discharged continuously to the roof vent; a flammable plume can form near ignition sources or air intakes while the receiver and vent piping are chilled | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.3.2.S1 FA-1 inline vent device without confirmed flame-arrestor credit; 1.3.2.S2 roof discharge location | 4 | 1 | R1 | 1.3.2.R1 Verify roof vent dispersion and ignition-source separation for continuous SV-21.2 open failure | 1.3.2 FA-1 function is not fully defined and is therefore not credited as an IPL
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.3 SV-21.2 fails open or leaks on the receiver vent line to roof causing continuous expansion cooling of TK-500L contents | 1.3.3 Rapid cooling of TK-500L nozzles and vent manifold can create thermal stress; loss of containment of hydrogen-containing gas may occur with fire or explosion potential | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.3.3.S1 Stainless-steel receiver construction; 1.3.3.S2 routine mechanical integrity inspection | 4 | 1 | R1 | 1.3.3.R1 Confirm TK-500L and vent manifold minimum design temperature for full depressurization through SV-21.2 | 1.3.3 Minimum metal temperature check is required for credible blowdown cooling
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.3 SV-21.2 fails open or leaks on the receiver vent line to roof causing continuous expansion cooling of TK-500L contents | 1.3.4 Cold vent discharge can increase gas density and reduce dispersion at the roof outlet; personnel exposure to nitrogen-enriched or hydrogen-containing gas may occur near roof access points | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.4.S1 Discharge routed to roof; 1.3.4.S2 site access control and gas hazard awareness | 3 | 1 | R2 | 1.3.4.R1 Assess roof vent exclusion zone and need for fixed gas detection near access or air intakes | 1.3.4 Review should consider both flammability and oxygen-deficiency hazards
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.3 SV-21.2 fails open or leaks on the receiver vent line to roof causing continuous expansion cooling of TK-500L contents | 1.3.5 Depressurization cooling can disturb H2A-1 measurement and receiver mixing; hydrogen-rich residual gas may be delivered to the process if normal outlet remains available | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.3.5.S1 H2A-1 concentration monitoring; 1.3.5.S2 SV-21.1 emergency outlet isolation logic | 4 | 1 | R1 | 1.3.5.R1 Evaluate whether SV-21.2 open feedback or low receiver pressure should force SV-21.1 closure | 1.3.5 Existing emergency logic is not credited because the initiating failure is outside the confirmed high-H2 trigger basis
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.4 SV-21.3 opens spuriously causing high nitrogen purge flow and expansion cooling into the receiver outlet header | 1.4.1 Cold nitrogen purge dilutes TK-500L contents while the normal outlet remains aligned; the downstream process can receive high-nitrogen low-temperature gas outside its design basis | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.1.S1 H2A-1 concentration indication; 1.4.1.S2 PI-OUT-1 local pressure indication | 3 | 1 | R2 | 1.4.1.R1 Add abnormal N2 purge status alarm and define operator action for inadvertent SV-21.3 opening | 1.4.1 H2A-1 may show low H2 but no confirmed low-H2 trip is described
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.4 SV-21.3 opens spuriously causing high nitrogen purge flow and expansion cooling into the receiver outlet header | 1.4.2 Low-temperature nitrogen chills SV-21.1 and CV-12.1; valve-seat contraction can allow leakage of off-specification cold gas toward the downstream process | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.2.S1 CV-12.1 check valve; 1.4.2.S2 operator observation of pressure and concentration trends | 3 | 1 | R2 | 1.4.2.R1 Verify SV-21.1 and CV-12.1 seat materials and leakage class for cold nitrogen purge exposure | 1.4.2 Check valve is not credited as IPL for forward leakage of off-specification gas
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.4 SV-21.3 opens spuriously causing high nitrogen purge flow and expansion cooling into the receiver outlet header | 1.4.3 Excess cold nitrogen reduces hydrogen concentration below the required process value; downstream equipment may trip or create unstable operation due loss of fuel or reducing gas duty | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.3.S1 H2A-1 displayed concentration; 1.4.3.S2 HMI-1 operator interface | 3 | 1 | R2 | 1.4.3.R1 Confirm downstream process consequence of low-H2 gas and add interlock or alarm if instability has safety significance | 1.4.3 Downstream effect should be validated with process licensor or user
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.4 SV-21.3 opens spuriously causing high nitrogen purge flow and expansion cooling into the receiver outlet header | 1.4.4 Rapid cooling at the receiver outlet nozzle and purge header can produce thermal fatigue or cracking; mixed gas leakage may ignite if hydrogen concentration remains within flammable range | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.4.4.S1 Stainless-steel TK-500L construction; 1.4.4.S2 preventive maintenance on purge valves and receiver nozzles | 4 | 1 | R1 | 1.4.4.R1 Include inadvertent cold N2 purge in the minimum metal temperature and fatigue assessment for TK-500L nozzles | 1.4.4 Mechanical integrity review should include repeated spurious-purge cycling
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.4 SV-21.3 opens spuriously causing high nitrogen purge flow and expansion cooling into the receiver outlet header | 1.4.5 Continuous unintended purge can deplete the available nitrogen supply and cool the purge train; subsequent emergency flushing may be unavailable or delayed during a true high-H2 event | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.5.S1 PI-N2-1 local pressure indication; 1.4.5.S2 operator investigation after abnormal emergency sequence | 3 | 1 | R2 | 1.4.5.R1 Provide N2 supply low-pressure alarm and SV-21.3 status monitoring tied to emergency readiness checks | 1.4.5 Scenario is an asset and safety-readiness concern for the purge function
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.5 Internal restriction in MG-100-2ME(Ex) or partial blockage at SV-27 creates excessive local pressure drop and expansion cooling in the mixed-gas transfer line | 1.5.1 Mixed gas temperature at the TK-500L inlet falls sharply; SV-27 or the receiver inlet may ice or restrict further and reduce supply to the downstream process | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.1.S1 TK-500L buffer volume; 1.5.1.S2 PI-OUT-1 local receiver outlet pressure indication | 2 | 1 | R2 | 1.5.1.R1 Add inspection or differential-pressure monitoring for MG-100-2ME(Ex) and SV-27 restriction if fouling or icing is credible | 1.5.1 Operability impact may escalate if downstream process cannot tolerate supply interruption
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.5 Internal restriction in MG-100-2ME(Ex) or partial blockage at SV-27 creates excessive local pressure drop and expansion cooling in the mixed-gas transfer line | 1.5.2 Cold mixed gas causes thermal stress at the TK-500L inlet nozzle and transfer piping; loss of containment of hydrogen-containing gas can lead to flash fire or explosion | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.2.S1 S316L piping specification; 1.5.2.S2 Ex-rated mixer equipment | 4 | 1 | R1 | 1.5.2.R1 Confirm minimum metal temperature for the mixed-gas line and receiver inlet under maximum credible pressure drop | 1.5.2 Design verification should include the 6 m and 10 m local line runs around the mixer and receiver
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.5 Internal restriction in MG-100-2ME(Ex) or partial blockage at SV-27 creates excessive local pressure drop and expansion cooling in the mixed-gas transfer line | 1.5.3 Restriction and cooling disturb mixer performance; hydrogen concentration excursions may occur in the receiver before the gas becomes uniform | 4 | 1 | R1 | 1.5.3.1 H2A-1 high H2 detection with EC-1 closure of SV-21.1 and purge vent sequence (-1) | Yes | Yes | Yes | 1.5.3.S1 CD-1 and HMI-1 concentration display; 1.5.3.S2 operator investigation after failed recovery below 9 percent H2 | 4 | 2 | R2 | 1.5.3.R1 Verify analyzer sample location detects nonuniform receiver gas quickly enough for the 9 percent H2 emergency action | 1.5.3 IPL credit requires demonstrated response before hydrogen-rich gas reaches the process
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.5 Internal restriction in MG-100-2ME(Ex) or partial blockage at SV-27 creates excessive local pressure drop and expansion cooling in the mixed-gas transfer line | 1.5.4 Repeated cold cycling at SV-27 can harden seals and increase leakage past the valve; uncontrolled mixed gas transfer may continue during an emergency isolation demand | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.4.S1 EC-1 command to close SV-27 after unsuccessful 10 min recovery; 1.5.4.S2 planned valve maintenance | 3 | 1 | R2 | 1.5.4.R1 Include SV-27 cold-cycle leakage testing and proof of closure in the emergency shutdown maintenance program | 1.5.4 SV-27 is not credited because the initiating cold condition may degrade its sealing performance
H2/N2 Gas Mixing and Receiver Tank System from customer gas supplies through MG-100-2ME(Ex) to TK-500L receiver and outlet purge vent interfaces | Filtered and regulated H2 and N2 are mixed and buffered in TK-500L for 4.5-5 bar process supply with H2 monitoring emergency N2 purge and roof venting | Temperature | Less | 1. Low Temperature | 1.5 Internal restriction in MG-100-2ME(Ex) or partial blockage at SV-27 creates excessive local pressure drop and expansion cooling in the mixed-gas transfer line | 1.5.5 Cold dense mixed gas entering TK-500L can stratify and delay analyzer recognition of abnormal composition; downstream process may receive a transient off-specification gas pocket | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.5.S1 H2A-1 receiver concentration monitoring; 1.5.5.S2 TK-500L buffer capacity | 3 | 1 | R2 | 1.5.5.R1 Review receiver mixing assumptions and analyzer response for cold dense gas entry from MG-100-2ME(Ex) | 1.5.5 Additional study should confirm whether stratification is credible in the 500 L receiver
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.1 SV-21.1 fails closed or CV-12.1 sticks closed on the normal TK-500L outlet path | 1.1.1 Gas inventory accumulates in TK-500L while MG-100-2ME(Ex) continues feeding; receiver pressure can approach the 10 bar design limit; hydrogen-containing gas may release if containment is exceeded | 4 | 1 | R1 | 1.1.1.1 TK-500L mechanical design pressure margin against normal regulated 8 bar supply (-2) | Yes | Yes | Yes | 1.1.1.S1 PI-OUT-1 local pressure indication; 1.1.1.S2 HMI-1 operating display | 4 | 3 | R2 | 1.1.1.R1 Verify blocked outlet pressure case against TK-500L design pressure and upstream regulator maximum failure pressure | 1.1.1.A1 Confirm whether independent high pressure alarm or shutdown is required for outlet blockage
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.1 SV-21.1 fails closed or CV-12.1 sticks closed on the normal TK-500L outlet path | 1.1.2 Downstream Process loses normal mixed gas supply; dependent equipment may trip or shut down with production interruption and asset impact | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.2.S1 HMI-1 status indication; 1.1.2.S2 Operator monitoring of outlet pressure and process demand | 2 | 1 | R2 | 1.1.2.R1 Define operator response for loss of receiver outlet flow and blocked outlet diagnosis | 1.1.2.A1 Confirm downstream Process safe state for loss of H2/N2 supply
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.1 SV-21.1 fails closed or CV-12.1 sticks closed on the normal TK-500L outlet path | 1.1.3 Reopening the outlet after receiver accumulation can send a pressure and composition surge to the downstream Process; equipment may receive hydrogen rich gas outside the intended envelope | 3 | 1 | R2 | 1.1.3.1 H2A-1 high hydrogen alarm with trained operator response through CD-1 and HMI-1 (-1) | Yes | Yes | Yes | 1.1.3.S1 PI-OUT-1 local pressure indication; 1.1.3.S2 Operating procedure for restart after outlet isolation | 3 | 2 | R2 | 1.1.3.R1 Add restart checks for receiver pressure and H2 concentration before restoring SV-21.1 | 1.1.3.A1 Confirm alarm set point and operator response time for abnormal receiver composition
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.1 SV-21.1 fails closed or CV-12.1 sticks closed on the normal TK-500L outlet path | 1.1.4 Packed receiver inventory can discharge through weak fittings or small bore connections; a flammable H2/N2 cloud may form near the receiver and ignite | 4 | 1 | R1 | 1.1.4.1 TK-500L mechanical design pressure margin against normal regulated 8 bar supply (-2) | Yes | Yes | Yes | 1.1.4.S1 Stainless steel receiver construction; 1.1.4.S2 Routine leak inspection of receiver connections | 4 | 3 | R2 | 1.1.4.R1 Confirm inspection scope for threaded joints analyzer connections and valve manifolds on TK-500L | 1.1.4.A1 Verify hazardous area classification and ignition control around MG-100-2ME(Ex) and TK-500L
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.1 SV-21.1 fails closed or CV-12.1 sticks closed on the normal TK-500L outlet path | 1.1.5 Mixer outlet pressure increases because receiver discharge is blocked; MG-100-2ME(Ex) can trip or suffer connection damage with local gas release potential | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.5.S1 PI-OUT-1 pressure indication; 1.1.5.S2 MG-100-2ME(Ex) Ex-rated equipment selection | 3 | 1 | R2 | 1.1.5.R1 Confirm MG-100-2ME(Ex) maximum discharge pressure protection for blocked receiver outlet | 1.1.5.A1 Review vendor limits for mixer deadheaded or blocked discharge operation
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.2 SV-27 remains open after stop or emergency command and allows continued mixed gas feed into TK-500L | 1.2.1 Mixed gas continues entering TK-500L after inventory should be isolated; receiver pressure can rise and hydrogen-containing gas may be released from the receiver system | 4 | 1 | R1 | 1.2.1.1 EC-1 stops MG-100-2ME(Ex) after failed recovery sequence (-1); 1.2.1.2 TK-500L mechanical design pressure margin against normal regulated 8 bar supply (-2) | Yes | Yes | Yes | 1.2.1.S1 H2A-1 continuous concentration monitoring; 1.2.1.S2 PI-OUT-1 local pressure indication | 4 | 4 | R3 | 1.2.1.R1 Verify that mixer stop is independent from SV-27 final element failure and proof tested | 1.2.1.A1 Confirm SV-27 fail position and emergency closure diagnostics
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.2 SV-27 remains open after stop or emergency command and allows continued mixed gas feed into TK-500L | 1.2.2 Hydrogen rich mixture can continue to accumulate in TK-500L and pass to the downstream Process; downstream flammable atmosphere or explosion hazard can result | 5 | 1 | R1 | 1.2.2.1 H2A-1 with EC-1 closes SV-21.1 on high hydrogen concentration (-1) | Yes | Yes | Yes | 1.2.2.S1 CD-1 and HMI-1 indication; 1.2.2.S2 Procedure to investigate failed recovery after 10 min | 5 | 2 | R1 | 1.2.2.R1 Evaluate whether high hydrogen isolation of SV-21.1 requires SIL classification and proof testing | 1.2.2.A1 Final risk remains high without documented independence and response reliability
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.2 SV-27 remains open after stop or emergency command and allows continued mixed gas feed into TK-500L | 1.2.3 Emergency purge may be unable to reduce H2 concentration while inlet flow continues; prolonged roof venting can create an ignitable hydrogen cloud at the discharge location | 4 | 1 | R1 | 1.2.3.1 EC-1 stops MG-100-2ME(Ex) after high hydrogen recovery failure (-1) | Yes | Yes | Yes | 1.2.3.S1 Roof vent discharge location; 1.2.3.S2 FA-1 inline vent device of unconfirmed function | 4 | 2 | R2 | 1.2.3.R1 Verify roof vent dispersion and ignition source separation for sustained hydrogen release | 1.2.3.A1 Confirm FA-1 function and inspection requirements for hydrogen vent service
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.2 SV-27 remains open after stop or emergency command and allows continued mixed gas feed into TK-500L | 1.2.4 Repeated high inventory and pressure cycling can overstress the receiver inlet piping and valve bodies; leaks and unplanned maintenance may result | 3 | 1 | R2 | 1.2.4.1 TK-500L and connected stainless steel piping design pressure margin for regulated feed service (-2) | Yes | Yes | Yes | 1.2.4.S1 Routine mechanical integrity inspection; 1.2.4.S2 Local pressure indication near outlet header | 3 | 3 | R3 | 1.2.4.R1 Confirm cyclic pressure loading is within the mechanical design basis for receiver inlet piping | 1.2.4.A1 Include SV-27 leakage and fail open testing in preventive maintenance
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.2 SV-27 remains open after stop or emergency command and allows continued mixed gas feed into TK-500L | 1.2.5 Off-spec receiver inventory may require controlled depressurization to roof and system shutdown; production loss and extended troubleshooting can occur | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.5.S1 H2A-1 concentration trending; 1.2.5.S2 HMI-1 emergency sequence indication | 2 | 1 | R2 | 1.2.5.R1 Develop procedure for safe disposal and requalification of off-spec receiver gas | 1.2.5.A1 Confirm customer decision basis for leaving SV-21.2 open to empty the receiver
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.3 PV-H2-REG fails high and drives excessive hydrogen feed to MG-100-2ME(Ex) and TK-500L | 1.3.1 Excess hydrogen feed increases receiver inventory and pressure beyond the normal operating basis; loss of containment can create a flammable jet or cloud fire | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.3.1.S1 PI-H2-1 local pressure indication; 1.3.1.S2 H2A-1 concentration monitoring | 4 | 1 | R1 | 1.3.1.R1 Provide an independent high pressure protection basis for regulator fail high into TK-500L | 1.3.1.A1 Confirm maximum upstream H2 supply pressure and whether 10 bar vessel rating is adequate
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.3 PV-H2-REG fails high and drives excessive hydrogen feed to MG-100-2ME(Ex) and TK-500L | 1.3.2 Receiver hydrogen concentration can exceed the intended mixture limit and reach the downstream Process; ignition in downstream equipment can cause severe fire or explosion | 5 | 1 | R1 | 1.3.2.1 H2A-1 with EC-1 closes SV-21.1 and initiates N2 purge on 9 percent H2 condition (-1) | Yes | Yes | Yes | 1.3.2.S1 CD-1 and HMI-1 alarm display; 1.3.2.S2 CV-12.1 check valve on outlet path | 5 | 2 | R1 | 1.3.2.R1 Classify the high hydrogen analyzer trip and outlet isolation function under IEC 61511 or document equivalent reliability | 1.3.2.A1 Final risk remains high until the protective function reliability is demonstrated
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.3 PV-H2-REG fails high and drives excessive hydrogen feed to MG-100-2ME(Ex) and TK-500L | 1.3.3 Emergency venting of hydrogen rich gas to roof may become prolonged and concentrated; ignition at or near the discharge point can cause flame impingement and personnel exposure | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.3.3.S1 Roof vent elevation; 1.3.3.S2 FA-1 inline vent device with unconfirmed protective role | 4 | 1 | R1 | 1.3.3.R1 Perform vent dispersion review for regulator fail high hydrogen release to roof | 1.3.3.A1 Define exclusion zone and ignition control requirements at the roof discharge point
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.3 PV-H2-REG fails high and drives excessive hydrogen feed to MG-100-2ME(Ex) and TK-500L | 1.3.4 MG-100-2ME(Ex) receives an excessive H2 feed ratio and can deliver unstable mixture quality; mixer upset or connection leakage can produce a localized flammable atmosphere | 3 | 1 | R2 | 1.3.4.1 H2A-1 high hydrogen alarm with operator response through HMI-1 (-1) | Yes | Yes | Yes | 1.3.4.S1 PI-H2-1 local pressure indication; 1.3.4.S2 Ex-rated mixer model selection | 3 | 2 | R2 | 1.3.4.R1 Add documented operator action for abnormal H2 supply pressure and analyzer deviation | 1.3.4.A1 Confirm H2 analyzer calibration coverage for the expected concentration range
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.3 PV-H2-REG fails high and drives excessive hydrogen feed to MG-100-2ME(Ex) and TK-500L | 1.3.5 Receiver composition shifts toward hydrogen rich gas and product quality is lost; downstream Process operation may be interrupted for purge and requalification | 2 | 1 | R2 | 1.3.5.1 H2A-1 continuous analyzer alarm with operator response (-1) | Yes | Yes | Yes | 1.3.5.S1 Auto calibration feature on H2A-1; 1.3.5.S2 Control and Display indication | 2 | 2 | R3 | 1.3.5.R1 Establish acceptance criteria for returning TK-500L to service after high hydrogen excursion | 1.3.5.A1 Record analyzer proof test and calibration interval in the operating basis
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.4 SV-21.3 opens spuriously and admits continuous emergency N2 purge flow into the receiver header | 1.4.1 Continuous N2 addition increases gas inventory in TK-500L and can raise receiver pressure toward the design limit; release of mixed gas may occur if containment is exceeded | 4 | 1 | R1 | 1.4.1.1 TK-500L design pressure margin relative to regulated 8 bar N2 purge supply (-2) | Yes | Yes | Yes | 1.4.1.S1 PI-N2-1 local pressure indication; 1.4.1.S2 PI-OUT-1 local pressure indication | 4 | 3 | R2 | 1.4.1.R1 Verify fail closed or deenergized state for SV-21.3 and confirm purge pressure cannot exceed TK-500L design | 1.4.1.A1 Include SV-21.3 spurious opening in functional test scope
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.4 SV-21.3 opens spuriously and admits continuous emergency N2 purge flow into the receiver header | 1.4.2 Nitrogen dilution lowers the hydrogen concentration below the intended process mixture; downstream Process may receive off-spec gas and experience production upset | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.2.S1 H2A-1 continuous concentration indication; 1.4.2.S2 HMI-1 display of emergency valve status | 2 | 1 | R2 | 1.4.2.R1 Configure low hydrogen concentration alarm or operating limit if downstream Process requires composition control | 1.4.2.A1 Confirm acceptable H2/N2 composition range for the downstream Process
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.4 SV-21.3 opens spuriously and admits continuous emergency N2 purge flow into the receiver header | 1.4.3 Unintended nitrogen release from receiver fittings can displace oxygen in a confined or poorly ventilated area; personnel asphyxiation exposure may occur | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.3.S1 Compressed nitrogen SDS hazard communication; 1.4.3.S2 Routine leak checks | 3 | 1 | R2 | 1.4.3.R1 Confirm ventilation and oxygen deficiency hazard controls for nitrogen purge equipment locations | 1.4.3.A1 Add nitrogen asphyxiation warning to operating and maintenance procedures
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.4 SV-21.3 opens spuriously and admits continuous emergency N2 purge flow into the receiver header | 1.4.4 Added purge flow can drive a pressure surge through SV-21.1 and CV-12.1 to the downstream Process; sensitive downstream equipment may trip or be damaged | 3 | 1 | R2 | 1.4.4.1 TK-500L and outlet piping design pressure margin for regulated N2 purge service (-2) | Yes | Yes | Yes | 1.4.4.S1 PI-OUT-1 local pressure indication; 1.4.4.S2 Downstream Process interface monitoring by others | 3 | 3 | R3 | 1.4.4.R1 Confirm downstream Process maximum allowable pressure for inadvertent N2 purge admission | 1.4.4.A1 Define interface responsibility for pressure protection downstream of CV-12.1
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.4 SV-21.3 opens spuriously and admits continuous emergency N2 purge flow into the receiver header | 1.4.5 N2 purge can displace hydrogen-containing inventory toward the roof vent or weak points; a flammable or oxygen deficient plume may expose personnel at elevated locations | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.4.5.S1 Roof vent routing; 1.4.5.S2 CV-12.3 check valve on N2 purge line | 4 | 1 | R1 | 1.4.5.R1 Review vent routing and access controls for inadvertent purge discharge scenarios | 1.4.5.A1 Confirm whether SV-21.2 opens during spurious SV-21.3 events or only during analyzer initiated emergency
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.5 SV-21.2 fails closed or MV-TK-VENT is closed on the receiver vent path during emergency purge and flush demand | 1.5.1 Emergency purge gas cannot leave TK-500L through the roof vent path; receiver inventory and pressure rise with potential hydrogen-containing gas release from the system | 4 | 1 | R1 | 1.5.1.1 EC-1 closes SV-27 and stops MG-100-2ME(Ex) after failed recovery (-1); 1.5.1.2 TK-500L design pressure margin relative to regulated 8 bar N2 purge supply (-2) | Yes | Yes | Yes | 1.5.1.S1 PI-OUT-1 local pressure indication; 1.5.1.S2 HMI-1 emergency sequence indication | 4 | 4 | R3 | 1.5.1.R1 Proof test SV-21.2 opening on emergency demand and manage MV-TK-VENT normal open position | 1.5.1.A1 Consider car seal open or locked open management for MV-TK-VENT if it must remain available
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.5 SV-21.2 fails closed or MV-TK-VENT is closed on the receiver vent path during emergency purge and flush demand | 1.5.2 High hydrogen concentration persists because the receiver cannot be flushed to roof; if normal outlet isolation is not maintained downstream equipment can receive flammable gas | 5 | 1 | R1 | 1.5.2.1 H2A-1 with EC-1 closes SV-21.1 on 9 percent H2 condition (-1) | Yes | Yes | Yes | 1.5.2.S1 CD-1 and HMI-1 alarm display; 1.5.2.S2 Procedure to investigate failed 10 min recovery | 5 | 2 | R1 | 1.5.2.R1 Add independent confirmation that SV-21.1 is closed during failed vent or purge recovery | 1.5.2.A1 Final risk remains high if outlet isolation reliability is not independently demonstrated
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.5 SV-21.2 fails closed or MV-TK-VENT is closed on the receiver vent path during emergency purge and flush demand | 1.5.3 Receiver cannot be emptied or requalified by the intended emergency flush route; extended outage and manual intervention are required | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.3.S1 H2A-1 analyzer trend; 1.5.3.S2 Control and Display status indication | 2 | 1 | R2 | 1.5.3.R1 Develop contingency procedure for safe depressurization when SV-21.2 or MV-TK-VENT is unavailable | 1.5.3.A1 Define authorization and gas testing requirements before manual venting or maintenance
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.5 SV-21.2 fails closed or MV-TK-VENT is closed on the receiver vent path during emergency purge and flush demand | 1.5.4 Hydrogen-containing gas remains trapped upstream of the blocked vent path; later opening of the path can release a concentrated flammable cloud to the roof discharge | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.4.S1 FA-1 inline vent device with unconfirmed function; 1.5.4.S2 Roof discharge routing | 4 | 1 | R1 | 1.5.4.R1 Require controlled vent reopening steps with concentration verification and ignition source control | 1.5.4.A1 Confirm FA-1 suitability for delayed release of hydrogen rich gas
H2/N2 Gas Mixing and Receiver Tank System including MG-100-2ME(Ex) and TK-500L | Filtered H2 and N2 are pressure regulated mixed and buffered in TK-500L at maximum 10 bar before delivery at 4.5-5 bar with analyzer based emergency isolation purge and roof venting | Level | More | 1. High Level | 1.5 SV-21.2 fails closed or MV-TK-VENT is closed on the receiver vent path during emergency purge and flush demand | 1.5.5 Operators may attempt local depressurization or troubleshooting while TK-500L contains pressurized H2/N2 inventory; personnel can be exposed to fire or nitrogen asphyxiation hazards | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.5.5.S1 Emergency alarm indication; 1.5.5.S2 Hydrogen and nitrogen SDS hazard communication | 4 | 1 | R1 | 1.5.5.R1 Establish emergency response procedure prohibiting local intervention until isolation depressurization and gas testing are complete | 1.5.5.A1 Train operators on invisible hydrogen flame hazard and oxygen displacement risk during emergency purge failures
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.1 SV-27 fails closed on the mixed gas inlet to TK-500L | 1.1.1 Receiver gas inventory falls below the intended buffer volume; downstream H2/N2 supply becomes unstable and the process can trip on loss of feed | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.1.S1 PI-OUT-1 local pressure indication; 1.1.1.S2 Control and Display trend monitoring | 2 | 1 | R2 | 1.1.1.R1 Add an independent low receiver pressure alarm with defined operator response | 1.1.1.CA1 Verify SV-27 failure position and shutdown response in the operating cause and effect matrix
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.1 SV-27 fails closed on the mixed gas inlet to TK-500L | 1.1.2 MG-100-2ME(Ex) continues to discharge against the closed inlet path; package backpressure can rise and create hydrogen-containing leakage from weak fittings | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.2.S1 Upstream pressure regulation at approximately 8 bar; 1.1.2.S2 PI-H2-1 and PI-N2-1 local indications | 3 | 1 | R2 | 1.1.2.R1 Confirm mixer outlet blocked-in pressure protection and alarm basis | 1.1.2.CA1 Review SV-27 closed position diagnostics and maintenance testing
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.1 SV-27 fails closed on the mixed gas inlet to TK-500L | 1.1.3 Continued outlet drawdown depressurizes TK-500L; reverse ingress from the process interface can dilute the receiver with air and form a flammable hydrogen mixture | 4 | 1 | R1 | 1.1.3.1 CV-12.1 process outlet check valve prevents reverse flow into TK-500L (-1) | Yes | Yes | Yes | 1.1.3.S1 PI-OUT-1 local pressure indication; 1.1.3.S2 downstream process operating surveillance | 4 | 2 | R2 | 1.1.3.R1 Verify CV-12.1 inspection frequency and reverse-flow design basis for low receiver pressure | 1.1.3.CA1 Include low receiver inventory with reverse flow in the operating abnormal situation procedure
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.1 SV-27 fails closed on the mixed gas inlet to TK-500L | 1.1.4 Receiver inventory depletion reduces composition buffering; an off-spec hydrogen concentration transient can reach the downstream process before stable recovery | 3 | 1 | R2 | 1.1.4.1 H2A-1 high H2 detection with EC-1 outlet isolation and mixer stop action (-1) | Yes | Yes | Yes | 1.1.4.S1 Control and Display indication; 1.1.4.S2 HMI-1 abnormal condition display | 3 | 2 | R2 | 1.1.4.R1 Confirm H2A-1 proof test and auto-calibration verification interval | 1.1.4.CA1 Check that emergency logic covers low receiver inventory with abnormal composition
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.1 SV-27 fails closed on the mixed gas inlet to TK-500L | 1.1.5 Rapid receiver drawdown causes pressure cycling in the 1 inch stainless steel piping; gasket loading can fluctuate and a small hydrogen-containing release may occur | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.1.5.S1 Scheduled mechanical integrity checks; 1.1.5.S2 pressure indication at receiver outlet header | 3 | 1 | R2 | 1.1.5.R1 Define allowable pressure cycling limits for TK-500L and associated piping | 1.1.5.CA1 Inspect small-bore connections and vent manifold joints after abnormal drawdown events
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.2 SV-21.1 fails open on the normal receiver outlet path | 1.2.1 TK-500L inventory is withdrawn faster than intended; the downstream process receives an unstable gas supply and may shut down on low feed pressure | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.1.S1 PI-OUT-1 local pressure indication; 1.2.1.S2 downstream process monitoring | 2 | 1 | R2 | 1.2.1.R1 Add low receiver pressure alarm or low supply pressure trip if process upset consequence is confirmed | 1.2.1.CA1 Confirm normal outlet valve stroke testing and fail-safe position
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.2 SV-21.1 fails open on the normal receiver outlet path | 1.2.2 Abnormal receiver gas can continue to the process despite depleted inventory; a flammable hydrogen-rich mixture may be introduced to equipment not intended for that composition | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.2.2.S1 H2A-1 analyzer indication; 1.2.2.S2 HMI-1 alarm display; 1.2.2.S3 operator investigation after failed recovery | 4 | 1 | R1 | 1.2.2.R1 Provide an independent final isolation function or verify SV-21.1 closure reliability for high H2 and low inventory scenarios | 1.2.2.CA1 Treat SV-21.1 failed-open demand as a key protective function gap
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.2 SV-21.1 fails open on the normal receiver outlet path | 1.2.3 Receiver pressure can fall below downstream pressure; reverse process gas can enter TK-500L and create contamination or a flammable mixture in the receiver | 4 | 1 | R1 | 1.2.3.1 CV-12.1 process outlet check valve prevents reverse flow into the receiver (-1) | Yes | Yes | Yes | 1.2.3.S1 downstream process pressure monitoring; 1.2.3.S2 PI-OUT-1 local indication | 4 | 2 | R2 | 1.2.3.R1 Confirm CV-12.1 is suitable for hydrogen service and tested for seat leakage | 1.2.3.CA1 Add reverse-flow scenario to commissioning and maintenance test records
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.2 SV-21.1 fails open on the normal receiver outlet path | 1.2.4 MG-100-2ME(Ex) experiences unstable backpressure while the receiver is being overdrawn; mixer control instability can cause off-ratio gas and repeated trips | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.4.S1 mixer package monitoring; 1.2.4.S2 local feed pressure indicators PI-H2-1 and PI-N2-1 | 3 | 1 | R2 | 1.2.4.R1 Confirm mixer operating envelope for low receiver pressure and high outlet demand | 1.2.4.CA1 Include abnormal outlet drawdown in operator training
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.2 SV-21.1 fails open on the normal receiver outlet path | 1.2.5 Downstream equipment loses the intended buffer supply; loss of protective or process gas may create an unsafe operating state in the receiving unit | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.2.5.S1 downstream unit alarms; 1.2.5.S2 Control and Display status indication | 3 | 1 | R2 | 1.2.5.R1 Define downstream minimum supply pressure and automatic demand shutdown requirements | 1.2.5.CA1 Coordinate receiver low inventory response with downstream process procedures
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.3 SV-21.2 spuriously opens on the roof vent path | 1.3.1 Hydrogen-containing mixed gas vents from TK-500L to the roof; a flammable cloud can form near the discharge point and ignite if a competent ignition source is present | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.3.1.S1 roof vent elevation and discharge routing; 1.3.1.S2 FA-1 vent-line device if maintained for service | 4 | 1 | R1 | 1.3.1.R1 Verify roof vent dispersion and hazardous area classification for unintended SV-21.2 opening | 1.3.1.CA1 Confirm whether FA-1 is a flame arrester or other protective device and define inspection requirements
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.3 SV-21.2 spuriously opens on the roof vent path | 1.3.2 Receiver inventory is lost through the vent path; normal process gas delivery becomes interrupted and the downstream process can trip | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.2.S1 HMI-1 valve status display; 1.3.2.S2 PI-OUT-1 local pressure indication | 2 | 1 | R2 | 1.3.2.R1 Add open-valve diagnostic alarm for SV-21.2 during normal operation | 1.3.2.CA1 Confirm SV-21.2 fail position and solenoid health monitoring
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.3 SV-21.2 spuriously opens on the roof vent path | 1.3.3 Continued venting can draw air back through the roof vent when receiver pressure decays; air mixed with residual hydrogen in TK-500L can create an internal flammable atmosphere | 4 | 1 | R1 | 1.3.3.1 CV-12.2 vent-line check valve prevents reverse flow from the roof vent into TK-500L (-1) | Yes | Yes | Yes | 1.3.3.S1 FA-1 maintained in vent service; 1.3.3.S2 procedural control of vent line configuration | 4 | 2 | R2 | 1.3.3.R1 Verify CV-12.2 reverse-flow performance and leakage acceptance criteria | 1.3.3.CA1 Include roof vent backflow checks in preventive maintenance
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.3 SV-21.2 spuriously opens on the roof vent path | 1.3.4 Nitrogen-rich purge or mixed gas discharged at roof level can displace oxygen around maintenance access points and expose personnel to an asphyxiation atmosphere | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.4.S1 roof discharge location; 1.3.4.S2 site access control for vent areas | 3 | 1 | R2 | 1.3.4.R1 Assess need for roof area gas detection or access restriction during venting | 1.3.4.CA1 Update permit to work requirements for roof access near the vent outlet
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.3 SV-21.2 spuriously opens on the roof vent path | 1.3.5 Sustained high velocity venting can stress FA-1 and vent piping; damaged vent protection can impair future emergency flushing service | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.3.5.S1 vent line mechanical design; 1.3.5.S2 routine visual inspection of FA-1 and roof discharge piping | 3 | 1 | R2 | 1.3.5.R1 Confirm FA-1 and roof vent mechanical design for continuous inadvertent venting | 1.3.5.CA1 Record post-event inspection requirements after any unintended vent opening
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.4 PV-N2-REG fails closed on the nitrogen regulated feed | 1.4.1 Nitrogen make-up to MG-100-2ME(Ex) is lost; mixed gas production falls below outlet demand and TK-500L inventory decreases until process supply is interrupted | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.4.1.S1 PI-N2-1 local pressure indication; 1.4.1.S2 intake filter maintenance for F-N2 | 2 | 1 | R2 | 1.4.1.R1 Provide a low regulated N2 pressure alarm with operator response | 1.4.1.CA1 Verify regulator maintenance and spare parts strategy for PV-N2-REG
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.4 PV-N2-REG fails closed on the nitrogen regulated feed | 1.4.2 Hydrogen fraction in the reduced receiver inventory can rise above the intended limit; the receiver and outlet header may contain a flammable hydrogen-rich gas | 4 | 1 | R1 | 1.4.2.1 H2A-1 high H2 detection with EC-1 closure of SV-21.1 and mixer stop action (-1) | Yes | Yes | Yes | 1.4.2.S1 HMI-1 alarm display; 1.4.2.S2 Control and Display indication | 4 | 2 | R2 | 1.4.2.R1 Confirm H2A-1 trip set point and functional proof test for high H2 at 9 percent | 1.4.2.CA1 Verify that loss of N2 supply does not inhibit outlet isolation command
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.4 PV-N2-REG fails closed on the nitrogen regulated feed | 1.4.3 Emergency purge gas is not available when receiver inventory is low; hydrogen-rich gas can remain in TK-500L and the vent header after a failed recovery attempt | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.4.3.S1 H2A-1 analyzer; 1.4.3.S2 emergency procedure requiring investigation after failed recovery | 4 | 1 | R1 | 1.4.3.R1 Provide independent low N2 purge pressure trip or alarm before relying on emergency flushing | 1.4.3.CA1 Treat N2 regulator failure as a common vulnerability for mixing and purge functions
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.4 PV-N2-REG fails closed on the nitrogen regulated feed | 1.4.4 Downstream process can receive H2-rich off-ratio gas while receiver inventory decays; equipment not designed for the higher hydrogen concentration may be exposed | 3 | 1 | R2 | 1.4.4.1 H2A-1 high H2 detection with EC-1 normal outlet isolation command (-1) | Yes | Yes | Yes | 1.4.4.S1 Control and Display concentration indication; 1.4.4.S2 downstream operating monitoring | 3 | 2 | R2 | 1.4.4.R1 Confirm SV-21.1 closure demand is included in the high H2 cause and effect test | 1.4.4.CA1 Define downstream notification actions for high H2 during low inventory
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.4 PV-N2-REG fails closed on the nitrogen regulated feed | 1.4.5 Loss of nitrogen sweep leaves stagnant hydrogen-rich gas in TK-500L at reduced inventory; later opening or maintenance can expose personnel to flammable gas | 4 | 1 | R1 | No credited IPL identified | No | No | No | 1.4.5.S1 permit to work gas testing; 1.4.5.S2 H2A-1 indication before intervention | 4 | 1 | R1 | 1.4.5.R1 Require verified inerting and gas-free testing before opening the receiver after N2 supply failure | 1.4.5.CA1 Add N2 loss recovery steps to maintenance isolation procedures
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.5 PV-H2-REG fails closed on the hydrogen regulated feed | 1.5.1 Hydrogen feed to MG-100-2ME(Ex) is lost; mixed gas make-up to TK-500L decreases and the downstream process loses the intended gas supply | 2 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.1.S1 PI-H2-1 local pressure indication; 1.5.1.S2 F-H2 filter maintenance | 2 | 1 | R2 | 1.5.1.R1 Provide low regulated H2 pressure alarm and defined shutdown response | 1.5.1.CA1 Verify PV-H2-REG inspection and set point control
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.5 PV-H2-REG fails closed on the hydrogen regulated feed | 1.5.2 Receiver gas becomes nitrogen-rich as inventory falls; downstream equipment may be inerted unexpectedly and nitrogen discharge at the use point can create asphyxiation exposure | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.2.S1 downstream process monitoring; 1.5.2.S2 Control and Display indication | 3 | 1 | R2 | 1.5.2.R1 Confirm whether low H2 concentration detection or analyzer low alarm is required | 1.5.2.CA1 Include nitrogen asphyxiation risk in downstream abnormal gas procedures
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.5 PV-H2-REG fails closed on the hydrogen regulated feed | 1.5.3 Continued normal outlet demand depressurizes TK-500L; reverse air or process gas ingress can create a flammable mixture when hydrogen service is restored | 4 | 1 | R1 | 1.5.3.1 CV-12.1 process outlet check valve prevents reverse flow into TK-500L (-1) | Yes | Yes | Yes | 1.5.3.S1 PI-OUT-1 local pressure indication; 1.5.3.S2 startup procedure after feed loss | 4 | 2 | R2 | 1.5.3.R1 Add restart purge and analyzer verification requirements after H2 feed loss | 1.5.3.CA1 Verify CV-12.1 leakage testing and documentation
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.5 PV-H2-REG fails closed on the hydrogen regulated feed | 1.5.4 MG-100-2ME(Ex) can cycle or trip on inadequate H2 feed while receiver inventory is low; pressure transients may promote small releases at filter or regulator connections | 3 | 1 | R2 | No credited IPL identified | No | No | No | 1.5.4.S1 intake filter and regulator maintenance; 1.5.4.S2 local pressure indications PI-H2-1 and PI-OUT-1 | 3 | 1 | R2 | 1.5.4.R1 Define trip and restart logic for low H2 feed pressure | 1.5.4.CA1 Inspect H2 feed joints after repeated low feed pressure cycling
H2/N2 Gas Mixing and Receiver Tank System TK-500L and MG-100-2ME(Ex) | Filtered and regulated H2 and N2 are mixed by MG-100-2ME(Ex) and buffered in TK-500L for controlled 4.5-5 bar supply with analyzer initiated isolation purge and roof venting | Level | Less | 1. Low Level | 1.5 PV-H2-REG fails closed on the hydrogen regulated feed | 1.5.5 Recovery of H2 feed into a depleted receiver can create a transient hydrogen-rich slug; downstream equipment may receive flammable off-spec gas during restart | 4 | 1 | R1 | 1.5.5.1 H2A-1 high H2 detection with EC-1 closure of SV-21.1 and mixer stop action (-1) | Yes | Yes | Yes | 1.5.5.S1 HMI-1 restart status display; 1.5.5.S2 operator verification of analyzer reading before lining up to process | 4 | 2 | R2 | 1.5.5.R1 Require controlled restart with receiver purge and verified H2 concentration before opening to process | 1.5.5.CA1 Add restart acceptance criteria to the operating procedure